|  | पंजीकृत कार्यालय :शक्ति सदन, कोटला रोड़, न्यू दिल्ली-110002 (Regd. Office Shakti Sadan, Kotla Road, New Delhi-110002) कार्यालय उपमहाप्रबंधक (एस.ओ.) Office of Dy. General Manager (SO) एस एल डी सी बिल्डिंग, मिंटो रोड़, न्यू दिल्ली-110002 SLDC Building, Minto Road, New Delhi-110002 Ph: 23221149 FAX No.23221012 |
| --- | --- |
| No. F./DTL/207 /DGM(SO)/10-11/ | Dated : 21.04.2010 |

Subject  : 	Minutes of the Meeting held on 06.04.2010 at SLDC

Dear Sir,   /  महोदय

The minutes of the meeting held on 06.04.2010 at SLDC with regard to installation of Capacitor banks, under frequency relay installation at DISCOMs, Accounting of Energy from Non-conventional energy sources etc. is enclosed for ready reference and further necessary action please.

Thanking you,

भवदीय   /  Yours faithfully

Encl. As above.

(वी.वेणुगोपाल)/(V. Venugopal )

(उपमहाप्रबंधक (एस.ओ.)/Dy. G. M. (SO)

List of addresses

- General Manager (O&M),DTL,Parkstreet, 220kV S/Stn.,New Delhi

- General Manager (Planning), DTL, Jhandewalan, Delhi

- General Manager, Badarpur Thermal Power Stn., Badarpur, New Delhi-44

- General Manager (Commercial), DTL

- General Manager, RPH

- General Manager, G.T.Station

- General Manager, Pragati Station

- CWE (Utilities), MES, Delhi Cantt., ND-10

- Addl. Vice President, System Operation, BSES, Balaji Estate, Kalkaji, New Delh

- Chief Engineer (Electrical-1), NDMC, Palika Kendra, New Delhi-1

- Chief Engineer (Electrical-2), NDMC, Palika Kendra, New Delhi-1

- Director (Comml.), NDMC, Palika Kendra, New Delhi-1

- Sh. Pillai Ramachandaran, HoD (PSC&M), NDPL, Shakti Nagar, Nangia Park, Delhi

- Sh. Arunabha Basu, Head (Technology), Cennet Building, Adjacent to 66/11kV Pitampura-3 Grid Building, Near PP Jewelers, Pitampura, Delhi-34.

- HOG, System Operation, NDPL, Cennet Building, Adjacent to 66/11kV Pitampura-3 Grid Building, Near PP Jewelers, Pitampura, Delhi-34.

- Sh. V. P. Garg, Addl. V. P. (EHV), BSES Yamuna Power Ltd., Shakti Kiran Building, Karkadooma, Delhi

- Sh. Ajay Kumar, Addl. V. P. (PP&MM), BSES Rajdhani Power Ltd., BSES Bhawan, 2nd Floor, Nehru Place, New Delhi-110019

- Sh. M. C. Sharma, Addl. V. P. (EHV), BSES Rajdhani Power Ltd., BSES Office, Harinagar Grid S/stn, New Delhi.

- General Manager (Commercial), National Thermal Power Corporation, NTPC NCR Headquarter, Sector-24, Noida, UP-201301

- Dy. G. M. (Metering & Prot.), DTL, 220kV S/stn Building, Parkstreet, New Delhi-1

Copy for favour of kind information to :

  - Secretary, DERC, Viniyamak Bhawan, C-Block, Shivalik, New Delhi-17

  - CMD, DTL

  - Member Secretary, NRPC

  - General Manager, NRLDC

  - Chairperson, New Delhi Municipal Council,Palika Kendra,Sansad Marg, New Delhi

  - CEO, BSES Rajdhani Power Ltd, BSES Bhawan, Nehru Place, New Delhi-110019

  - CEO, BSES Yamuna Power Ltd, Shakti Kiran Building, Karkardooma, New Delhi-92

  - CEO, North Delhi Power Ltd, 33kV Grid S/Stn, Hudson Lane, Kingsway Camp, Delhi-9

  - Chief Engineer(Utilities),CWE,MES, Kotwali Road, Near Gopi Nath Bazar, Delhi Cantt New Delhi-10

  - Managing Director, Indraprastha Power Generation Company Ltd (Genco) / Pragati Power Corporation Ltd (PPCL), Himadri, Rajghat Power House, New Delhi-110002

  - Dy. Secretary (Power), GNCTD

  - Director (Operations), DTL

  - Director (Tech.) IPGCL/PPCL

  - G. M. (SLDC)

  - Dy. G. M. (SCADA), Delhi SLDC

DELHI TRANSCO LTD.

(Regd. Office : Shakti Sadan, Kotla Road, New Delhi 110002)

[Office of Dy. General Manager (SO)]

Sub   :	Minutes of Meeting held at SLDC on 06.04.2010 at 11.00hrs. with regard to installation of additional capacitors, Under frequency relay installations at Discoms, Accounting of Energy from non-conventional energy sources etc.

Director (Operations), Delhi Transco Limited who chaired the meeting welcomed all the participants. He outlined the need of calling this special meeting looking into the urgency of the installation of additional capacitors looking into the increasing demand of reactive power following the onset of summer and to meet the dead line of installation of under frequency relays by Discoms as per the directive of DERC i.e. by 30.04.2010. After the brief opening remarks of the Chair the agenda was taken up for discussion.

List of the participants is enclosed as Annexure.

1. Installation of additional capacitors

SLDC indicated that as per NRPC study Delhi has to install additional 569MVAR in its system during the year 2010-11. The capacitors are required to be installed at load centers by Distribution Licensees. As per the assessment based on the last year MVAR consumption DTL has suggested the Distribution Licensees to install additional capacitors in their system as under :

|  | Utility | Additional capacity to be installed in MVAR |
| --- | --- | --- |
| 1 | NDPL | 150MVAR |
| 2 | BRPL | 300MVAR |
| 3 | BYPL | Nil |
| 4 | NDMC | 150MVAR |
| 5 | MES | Nil |
|  | Total | 600MVAR |

Meeting in this regard also held in the office of G. M. (Planning), DTL on 04.09.2009 in which all Distribution Licensees have given the plans for installation of capacitors in their system as under :

| Utility | Additional capacity to be installed in MVAR |
| --- | --- |
|  | 2009-2010 | 2010-2011 |
| NDPL | 21.6 | 64.8 |
| BRPL | 124.2 | 0 |
| BYPL | 54 | 0 |
| NDMC | 100.8 | 50.4 |
| MES | 0 | 0 |
| Total | 300.6 | 115.2 |

It was also pointed out that all Distribution Licensees draw large quantum of reactive power from the grid. SLDC also provided the status of reactive energy drawal by Distribution Licensees viz-a-viz the active energy during the period 01.04.2007 to 31.01.2010. The details are as under :

DETAILS OF REACTIVE ENERGY DRAWAL FROM THE GRID DURING 2007-08 & 2008-09

All figures in MUs (Reactive)

| S. No | Utility | April'07 – Sept'08 | Oct-08 | Nov-08 | Dec-08 | Jan-09 | Feb-09 | Mar-09 | Total | %age |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | NDPL | 810 | 72 | 63 | 48 | 44 | 55 | 62 | 1154 | 31.73 |
| 2 | BRPL | 564 | 59 | 57 | 48 | 44 | 52 | 67 | 891 | 24.50 |
| 3 | BYPL | 346 | 21 | 28 | 37 | 34 | 38 | 49 | 553 | 15.20 |
| 4 | NDMC | 733 | 39 | 27 | 26 | 25 | 24 | 31 | 905 | 24.88 |
| 5 | MES | 107 | 4 | 4 | 5 | 5 | 4 | 5 | 134 | 3.68 |
|  | Total | 2560 | 195 | 179 | 164 | 152 | 173 | 214 | 3637 | 100.00 |

DETAILS OF ACTIVE ENERGY DRAWAL DURING 2007-08 & 2008-09

All figures in MUs

| S.No. | Utility | April'07 – Sept'08 | Oct-08 | Nov-08 | Dec-08 | Jan-09 | Feb-09 | Mar-09 | Total | %age |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | NDPL | 9829 | 536 | 426 | 454 | 472 | 419 | 464 | 12600 | 28.50 |
| 2 | BRPL | 14450 | 762 | 585 | 614 | 653 | 552 | 620 | 18236 | 41.24 |
| 3 | BYPL | 8338 | 461 | 349 | 353 | 375 | 325 | 367 | 10567 | 23.90 |
| 4 | NDMC | 1940 | 106 | 75 | 77 | 84 | 69 | 80 | 2431 | 5.50 |
| 5 | MES | 293 | 15 | 13 | 16 | 19 | 14 | 13 | 383 | 0.87 |
|  | Total | 34849 | 1880 | 1448 | 1514 | 1603 | 1379 | 1545 | 44218 | 100.00 |

MONTH-WISE DETAILS OF REACTIVE ENERGY DRAWAL FROM THE GRID DURING 2009-10 (upto Jan)

All figures in MUs (Reactive)

| S. No. | Utility | Apr-09 | May-09 | Jun-09 | Jul-09 | Aug-09 | Sep-09 | Oct-09 | Nov-09 | Dec-09 | Jan-10 | Total | %age |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | NDPL | 63.53 | 54.78 | 44.32 | 47.42 | 58.01 | 49.31 | 40.17 | 35.61 | 31.12 | 32.57 | 456.84 | 25.33 |
| 2 | BRPL | 67.79 | 51.85 | 55.53 | 38.82 | 66.54 | 66.34 | 89.42 | 82.25 | 80.00 | 60.22 | 658.76 | 36.53 |
| 3 | BYPL | 49.15 | 27.49 | 27.83 | 20.07 | 20.92 | 27.95 | 36.32 | 47.15 | 44.94 | 37.59 | 339.42 | 18.82 |
| 4 | NDMC | 36.55 | 33.09 | 32.46 | 34.54 | 36.54 | 29.97 | 27.71 | 22.46 | 20.13 | 21.99 | 295.45 | 16.38 |
| 5 | MES | 5.52 | 6.27 | 6.28 | 4.87 | 5.92 | 5.45 | 5.28 | 4.32 | 4.26 | 4.92 | 53.09 | 2.94 |
|  | Total | 222.54 | 173.47 | 166.42 | 145.73 | 187.94 | 179.02 | 198.91 | 191.79 | 180.44 | 157.2900 | 1803.56 | 100.00 |

MONTH-WISE DETAILS OF ACTIVE ENERGY DRAWAL DURING 2009-10 (upto Jan)

All figures in MUs

| S.No. | Utility | Apr-09 | May-09 | Jun-09 | Jul-09 | Aug-09 | Sep-09 | Oct-09 | Nov-09 | Dec-09 | Jan-10 | Total | %age |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | NDPL | 543 | 645 | 685 | 732 | 707 | 628 | 558 | 472 | 483 | 522 | 5974 | 29.00 |
| 2 | BRPL | 755 | 971 | 996 | 1076 | 1026 | 881 | 735 | 584 | 636 | 727 | 8388 | 40.73 |
| 3 | BYPL | 454 | 563 | 585 | 632 | 605 | 530 | 455 | 357 | 371 | 416 | 4968 | 24.12 |
| 4 | NDMC | 100 | 124 | 130 | 141 | 132 | 115 | 99 | 75 | 80 | 94 | 1088 | 5.28 |
| 5 | MES | 15 | 18 | 19 | 20 | 19 | 17 | 15 | 14 | 18 | 23 | 177 | 0.86 |
|  | Total | 1866 | 2321 | 2415 | 2602 | 2489 | 2172 | 1862 | 1501 | 1588 | 1782 | 20595 | 100.00 |

SLDC further clarified that as per the data available with it inspite of heavy reactive power drawal from the grid and the assurance by DISCOMs to install additional capacity as on date not a single additional capacitor have been installed. SLDC requested the Distribution Licensees to update the status. The Distribution Licensees accordingly provided the following status.

NDPL

NDPL representative indicated that during the year 2009-10 the capacity to the tune of 72.3MVAr has been revived by repairing defective capacities as under :

| Sl. No. | Station | Voltage | MVAR re-commissioned |
| --- | --- | --- | --- |
| 1 | Bawana Clear Water Grid | 11kV | 10.8 |
| 2 | DSIDC-2 Grid | 11kV | 9.0 |
| 3 | Narela Grid | 11kV | 9.0 |
| 4 | Tripolia Grid | 11kV | 6.0 |
| 5 | Badli Grid | 11kV | 17.5 |
| 6 | RG-23 Grid | 11kV | 20 |
|  | Total |  | 72.3 |

The capacity has further been added to the tune of 23MVAr by upgrading the existing capacity in the following grid sub-stations

| Sr. No | Station | Voltage level in kV | MVAR added |
| --- | --- | --- | --- |
| 01 | SMB Khosla Grid Station | 11 | 0.6 |
| 02 | Azadpr Grid Station | 11 | 5.2 |
| 03 | Ranibagh Grid Station | 11 | 1.2 |
| 04 | Wzp-I Grid Station | 11 | 4.0 |
| 05 | PP-3 Grid Station | 11 | 1.8 |
| 06 | Rampura Grid Station | 11 | 0.6 |
| 07 | Haidepur Grid Station | 11 | 1.2 |
| 08 | Trinagar Grid Station | 11 | 2.4 |
| 09 | Ashok Vihar Grid Station | 11 | 2.4 |
| 10 | RG-I Grid Station | 11 | 0.6 |
| 11 | Gulabi Bagh Grid Station | 11 | 1.2 |
| 12 | MGP-1 Grid Station | 11 | 0.6 |
| 13 | GTK Grid Station | 11 | 1.2 |
|  | Total |  | 23.0 |

It has further added 36MVAr capacity in the new grid S/stns during the year 2009-10 as under :

| Sr. No | Station | Voltage level in kV | MVAR added |
| --- | --- | --- | --- |
| 01 | SMB Facility Center Grid Station | 11 | 7.2 |
| 02 | Tiggipore Grid Station | 11 | 7.2 |
| 03 | DIFR Grid Station | 11 | 7.2 |
| 04 | Ghewra Grid Station | 11 | 7.2 |
| 05 | DU Grid | 11 | 7.2 |
|  | Total |  | 36 |

It was further indicated that they are expected to add 57.6MVAr capacity by June 2010 as detailed hereunder :

| Sr. No | Station | Voltage level in kV | MVAR added |
| --- | --- | --- | --- |
| 01 | Bhalswa | 11 | 7.2 |
| 02 | Kirti Nagar Grid Station | 11 | 7.2 |
| 03 | Gulabi Bagh Grid Station | 11 | 7.2 |
| 04 | Bawana 06 Grid Station | 11 | 14.4 |
| 05 | Rg-06 Grid Station | 11 | 7.2 |
| 06 | Pusa Grid Station | 11 | 7.2 |
| 07 | Rohini DC-1 Grid Station | 11 | 7.2 |
|  | Total |  | 57.6 |

The re-commissioning of capacitor bank at DSIIDC-I by 15th April 2010 would enhance the working capability by 20MVAr. (The capacitor bank has not yet been revived)

Thus in summary 131.5MVAr capacity has already been enhanced in the system so far. Another 21.6MVAr will be added before June 2010 in phased manner and 36MVAr will be added during this year with the approval of DERC. It was also indicated that the switching of most of the 11kV capacitor bank for their effective utilization is through auto mated switching and has given the positive result in the reactive power consumption.

They requested SLDC/DTL to take up the matter with NRPC so that the reimbursement facility of CAPEX expenditure for capacitor bank installation can be extended to them.

They requested the intervention of DTL as wide voltage fluctuation at Subzi Mandi Grid S/stn is occurring due to which about 40-50MVAr capacity can not be utilized properly. They have that the present position of capacitor bank in NDPL system is as under :

| Voltage level in kV | Installed Capacity MVAR |
| --- | --- |
|  | North | North - Center | North - West | Total |
| 11kV | 183.2 | 242.16 | 156.85 | 582.21 |
| 33kV | 13.26 | 0 | 20 | 33.26 |
| 66kV | 0 | 40 | 100 | 140 |
| Total | 196.46 | 282.16 | 276.85 | 755.47 |
| 440V(LT) | 119 |

BRPL

BRPL representative indicated that they have added 27MVAr capacity during the year 2009-10 as under :

| Sr. No | Location | Voltage level in kV | No. of Bank | MVAR Capacity proposed to be installed | Target |
| --- | --- | --- | --- | --- | --- |
| 01 | Vasant Vihar | 11 | 1 | 5.4 | Commissioned on 26.10.09 |
| 02 | Okhla Ph-II | 11 | 1 | 5.4 | Commissioned on 08.12.09 |
| 03 | G-I5 Pappankalan | 11 | 2 (5.4) | 10.8 | Commissioned on 04.02.10 |
| 04 | Vishal WDCC | 11 | 1 | 5.4 | Commissioned on 26.02.10 |
|  | Alaknanda | 11 | 1 | 5.4 | Commissioned on 02.02.10 |
|  | Total |  |  | 32.4 |  |

Proposed to be commissioned in 2010-11

| Sr. No | Location | Voltage level in kV | No. of Bank | MVAR Capacity proposed to be installed | Target |
| --- | --- | --- | --- | --- | --- |
| 01 | G-6 Pappankalan | 11 | 1 | 5.4 | June-10 |
| 02 | Bhikaji Cama Place | 11 | 1 | 5.4 | May-10 |
| 03 | Sarai Julaina | 11 | 1 | 5.4 | May-10 |
| 04 | NDSE-I | 11 | 1 | 5.4 | May-10 |
| 05 | NDSE-II | 11 | 1 | 5.4 | May-10 |
| 06 | Jasola | 11 | 1 | 5.4 | May-10 |
| 07 | C-Dot | 11 | 1 | 5.4 | May-10 |
| 08 | D.C. Saket | 11 | 1 | 5.4 | May-10 |
| 09 | East of Kailash | 11 | 1 | 5.4 | June-10 |
| 10 | Bijwasan | 11 | 1 | 5.4 | May-10 |
| 11 | Nangloi Water Works | 11 | 1 | 5.4 | June-10 |
| 12 | Mayapuri | 11 | 1 | 5.4 | June-10 |
| 13 | Mukherjee Park | 11 | 1 | 5.4 | June-10 |
| 14 | Udyog Nagar-I | 11 | 1 | 5.4 | May-10 |
| 15 | Udyog Nagar-II | 11 | 1 | 5.4 | June-10 |
| 16 | Pappankalan-II 220kV | 11 | 2(5.4) | 10.8 | May-10 |
|  | Total |  | 18 | 91.8 |  |

As they have planned additional 97.2MVAr capacity by June 2010.

It was further clarified that due to space constraints in the existing S/stns to meet the target fixed by DTL the scheme for enhancement of exiting capacity need to be carried out. They have plans for switched capacitors at LT level also to meet the voltage problem as specified by DTL.

BYPL

Even though no additional capacity is required to be added in the system they have added 5.04MVAr capacity during the year 2009-10 as detailed hereunder :-

| Sr. No | Location | Voltage level in kV | No. of Bank | MVAR Capacity proposed to be installed | Target |
| --- | --- | --- | --- | --- | --- |
| 01 | Shankar road | 11 | 1 | 5.4 | Commissioned in March 10 |
|  | Total |  | 1 | 5.4 |  |

It was also indicated that 78.58MVAr capacity would be added during the year 2010-11 as under .

| S.NO. | NAME OF THE GRID | CAPACITY IN MVAR |
| --- | --- | --- |
| 1 | Ghonda Grid | 14.91 |
| 2 | Jama Masjid | 5.04 |
| 3 | CBD-I | 10.03 |
| 4 | PREET VIHAR | 5.4 |
| 5 | DWARAPURI | 5.4 |
| 6 | MAYUR VIHAR-II | 5.4 |
| 7 | GT ROAD | 5.4 |
| 8 | FAIZ ROAD | 5.4 |
| 9 | GB PANT | 5.4 |
| 10 | FOUNTAIN | 5.4 |
| 11 | SHASTRI PARK | 5.4 |
| 12 | TOWN HALL | 5.4 |
|  | Total | 78.58 |

NDMC

NDMC representative indicated that no additional capacity has been added during the year 2009-10. They have entrusted the work to PGCIL for upgradation of their system in which the additional capacitor installation is also envisaged. They have the ambitious plan of installation of 95.76 MVAr additional capacity during the year 2010-11 as detailed hereunder :

| Sr. No | Location | Voltage level in kV | MVAR Capacity proposed to be installed | Target |
| --- | --- | --- | --- | --- |
| 01 | Vidyut Bhawan | 11kV | 5.04 | June 2010 |
| 02 | B.D. Marg | 11kV | 5.04 |  |
| 03 | Connaught Place | 11kV | 5.04 |  |
| 04 | Race Course | 11kV | 5.04 |  |
| 05 | Shahjahan Road | 11kV | 5.04 |  |
| 06 | National Archieve | 11kV | 5.04 |  |
| 07 | Mandi House | 11kV | 5.04 |  |
| 08 | Trauma Center | 11kV | 5.04 |  |
| 09 | Bapu Dham | 11kV | 5.04 |  |
| 10 | State Guest House | 11kV | 5.04 |  |
| 11 | Church Road | 11kV | 5.04X2=10.08 | June 2010 |
| 12 | Raja Bazar | 11kV | 5.04X2=10.08 |  |
| 13 | Jor Bagh (New S/Stn) | 11kV | 5.04X2=10.08 |  |
| 14 | Sanjay Camp (New S/Stn) | 11kV | 5.04X2=10.08 |  |
| 15 | Constitution Club (New S/Stn) | 11kV | 5.04X2=10.08 |  |
|  | Total |  | 100.80 |  |
| 16 | Janpath Lane (New S/Stn) | 11kV | 5.04X2=10.08 |  |
| 17 | Keventer Dairy | 11kV | 5.04X2=10.08 |  |
| 18 | IGNCA (New S/Stn) | 11kV | 5.04X3=15.12 |  |
| 19 | Delhi High Court (new S/Stn) | 11kV | 5.04X2=10.08 |  |
| 20 | Lady Harding Medical College (New S/Stn) | 11kV | 5.04 |  |
|  | Total for 2010-11 |  | 50.40 |  |

IPGCL

IPGCL representative indicated that they have 20MVAr capacity at RPH complex and is in healthy condition. However they informed that one Bay (no. 4) on which one 10MVAr capacitor is connected has been allocated to NDPL for drawing out Civil Line feeder. In such scenario this capacitor bank shall have to be decommissioned.

Reacting on the decommissioning of the capacitor bank at RPH, SLDC cautioned against the heavy reactive power demand following the decommissioning of IP generating units. The capacitor bank being spared at RPH be used at IP which may compensate to some extent the loss of reactive support due to decommissioning of IP generating units. Generating utility agreed the proposal subject to the completion of commercial formalities as the transfer of the capacitor from RPH to IP involved the asset transfer from Genco to Transco.

Considering the plans of installation of additional capacitors and position of capacitors in Delhi is under :

Utility		Installed Capacity in MVAR

HT		LT

DTL		754		--

BRPL		1083		241

BYPL		765		89

NDPL		756		119

NDMC		106		30

MES		20		--

IPGCL		20		--

Total		3504		479

After considering the plans submitted by DISCOMs, Director (Operations) expressed the dismay over the situation as practically no appreciable additional capacity is envisaged before the ensuing summer. He specially mentioned about very slow progress of installation of capacitors in NDMC area whose reactive power demand is even equal to that of the active power demand. He specially mentioned about the reactive power consumption of the utility which is 25% of the total reactive consumption of Delhi where as the active power demand is only 6% of the total demand of Delhi. He further emphasized the need of maintenance of existing capacitors as well and all capacity should be made available to meet the reactive power demand. He cautioned the heavy penalty proposed by CERC in the new Indian Electricity Grid Code (IEGC) the pricing of reactive power drawal under low voltage condition of present level of 6.76Ps/KVRAh to 25Ps/KVARh. He further intimated that CERC has tighten the voltage profile also to ensure stability of the grid as under :

VOLTAGE – (KV rms)

|  | Existing Regulations | Proposed from 01.04.2010 |
| --- | --- | --- |
| Nominal | Maximum | Minimum | Maximum | Minimum |
| 765 | -- | -- | 800 | 728 |
| 400 | 420 | 360 | 420 | 380 |
| 220 | 245 | 200 | 245 | 198 |
| 132 | 145 | 120 | 145 | 122 |

In view of above he advised all utilities to pay attention to the capacity addition as well as proper maintenance and operation of existing capacitors to ensure the operation of the grid within the above limit of the voltage profile. Regarding Subzimandi problem expressed by NDPL he advised GM(O&M), DTL to set right the problem if any occurring in the grid S/stn. He further noticed about 76.08MVAr capacity is down in DTL system as detailed hereunder :

| Sr. No | Location | Capacitor Bank | Under Breakdown since | Remarks |
| --- | --- | --- | --- | --- |
| 1 | 220kV Gazipur | 5.04MVAR | 26.05.2009 | Due to problem in VCB |
| 2 | 220kV Mehrauli | 20MVAR-IV | 11.09.2009 | Bank dismantled for DMRC bays |
| 3 | 220kV Patparganj | 10MVAR-II | 09.07.2008 | Due to damage of Reactors & NCT |

| Sr. No | Location | Capacitor Bank | Under Breakdown since | Remarks |
| --- | --- | --- | --- | --- |
| 4 | 220kV Okhla | 20MVAR-II | 13.03.10 | Due to problem in breaker |
| 5 | 220kV Shalimarbagh | 10MVAR-II | 05.01.2010 | Due to VCB problem |
| 6 | 220kV Shalimarbagh | 6MVAR | 23.09.2009 | Due to VCB problem |
|  | 220kV Najafgarh | 5.04MVAR | 12.06.2009 | Due to VCB problem |
|  | Total | 76.08 |  |  |

He advised GM(O&M), DTL to expeditiously revive the capacitor banks under break down at the earliest.

He further drew attention to all stake holders that NRPC is monitoring the installation of additional capacity at regional level and requested all states to provide the status in the following formats as requested them :

| S. No. | Name of Sub-station | Capacitor MVAR | Whether financial approval obtained | If, Yes status of procurement | Schedule date of commissioning |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Yes/No | Date of floating of tenders | Whether tenders evaluated | Date of issue of purchase orders | Date of delivery |  |

He requested all the stake holders to provide the details in the above format before the next OCC meeting of NRPC. It was also requested that as per the NRPC requirement the position of Capacitor working be given to SLDC in the following format by last working day of the every month for onward transmission to NRPC.

| Sr. No. | Name of the Sub station | Status of the existing Capacitor Banks installed in system | Remarks |
| --- | --- | --- | --- |
|  |  | Capacity installed | Working capacity |  |

2	Compliance of Grid Connectivity Standards and Delhi Grid Code.

SLDC indicated that DERC vide their letters dated 20.11.2009 and 06.01.2010 has directed all Distribution Licensees to ensure the installation of under frequency relays before 30.04.2010 so as to facilitate grid security under conditions of falling grid frequency. It was indicated that a comprehensive scheme for Automatic Under Frequency Load Shedding Scheme is required to be drawn out with the approval of GCC to meet the stipulations of NRPC decision.

It has been decided in the 22nd & 23rd meeting of Operation Coordination Committee of NRPC held on 07.01.2008 and 08.02.2008 respectively. As per the decisions of the meeting ratified by NRPC (apex body) meeting the state wise quantum of load shedding envisaged through Under Frequency Load Shedding Scheme is as under :

All figures in MW

| State | Peak Met in 2006-07 | Flat frequency UFR | Total | Stage-I | Stage-II | Stage-III | Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 48.8 | 48.6 | 48.2 |  | 49.9Hz/0.1 Hz/sec | 49.9Hz/0.2 Hz/sec | 49.9Hz/0.3 Hz/sec |  |
| Punjab | 6558 | 180 | 220 | 250 | 650 | 430 | 490 | 490 | 1410 |
| Haryana | 4201 | 110 | 140 | 150 | 400 | 280 | 310 | 310 | 900 |
| Rajasthan | 4946 | 120 | 150 | 225 | 495 | 330 | 370 | 370 | 1070 |
| Delhi | 3736 | 110 | 140 | 150 | 400 | 250 | 280 | 280 | 810 |
| UP | 7531 | 190 | 240 | 275 | 705 | 500 | 280 | 280 | 1060 |
| Uttarakhand | 991 | 30 | 30 | 50 | 110 | 70 | 70 | 70 | 210 |
| HP | 873 | 20 | 20 | 75 | 115 | 50 | 70 | 70 | 190 |
| J & K | 1309 | 40 | 50 | 75 | 165 | 90 | 90 | 90 | 270 |
| UT Chandigarh | 247 | 0 | 10 | 0 | 10 | 0 | 50 | 50 | 100 |
| Total (Stage-I) | 30392 | 800 | 1000 | 1250 | 3050 | 2000 | 2010 | 2010 | 6020 |
| Stage-II | 26626.5 |  |  |  |  |  |  |  |  |

df/dt		Total in Western UP				810

df/dt		Total in Punjab/Haryana/HP/J & K/UT Chd	2870

Flat UFR	Total in Punjab/Haryana/HP/J & K/UT Chd	1340

The logic for working out is as under:

1)	For Stage-I at 0.1 Hz/sec, the same has been uniformly distributed in Northern Region in the ratio of peak MW load met in 2006-07. In UP it might be ensured that 50% of these relays are installed in western UP. (west of Lucknow/Panki/Unnao axis).

2) 	For Stage-II and Stage-III at 0.2 Hz/sec and 0.3 Hz/sec respectively, the same should act when there is a East-West separation within NR. Therefore these have been distributed in the ratio of loads in western part of the Northern Grid only. (taking western UP load as 50% of UP load).

3) 	Uttarakhand, HP, J&K and UT Chandigarh have been included in the list. These were not there earlier. The df/dt quantum for Punjab, Haryana, HP, J&K, UT Chandigarh as a whole would also take care of the winter off-peak conditions when hydro generation in this pocket is almost NIL leading to heavy imports from rest of the grid.

SLDC further intimated that the Distribution Licensees were requested vide letter no. F/DTL/207/SLDC/07-08/F-71/78 dated 02.02.2008 to provide the Under Frequency Relays at their system to shed the load at different frequencies as under :-

Frequency		NDPL		BYPL		BRPL		Total

Hz.			MW		MW		MW		MW

48.8			30		30		50		110

48.6			40		40		60		140

48.2			45		45		60		150

Relief through df/dt shall be provided by DTL through its own relays already installed at various sub-stations.  DTL shall block its flat mode of Under Frequency Relays operation after successful commissioning and satisfactory operation / required load relief through Under Frequency Relays scheme of Distribution Licensees is achieved.

SLDC requested all the Distribution Licensees to intimate the latest status in this regard. The utilities provided following status :

BRPL suggest following :-

i)	The df/dt operation shall be done at DTL sub-stations as indicated in the above referred letter.

ii)	All feeders emanating from the Grid sub-stations shall be categories into `A’ & `B’ Groups depending from the level of non desirability to shed load as determined by various factors.  The devision will tentatively be in the ratio of 70% and 30% respectively.

iii)	One set of Under Frequency Relay will be installed at Balaji and Malviya Nagar Grids (for redundancy), with PT supply input of Okhla and Mehrauli supplies respectively.  These relays shall be integrated with SCADA.  The threshold on these relays shall be set as per above requirement and stage wise trip output command generated.

iv)	In case of operation of the relay due to any of the triggers, a specified number of feeders to obtain the desired relief shall be selected sequentially from Group `A’.  The feeders which are already under outage or feeders which have been under outage at any point in the past 6 hours will be ignored at the time of selection.

v)	An automated group command will cause the actuation of the said scheme.

vi)	In case of this condition persisting beyond a period of one hour, the next set of feeders will be manually shed while restoring supply to the earlier shed feeders.

vii)	The scheme will continue in this fashion till all the available feeders in Group-`A’ are exhausted.  The feeders of Group `B’ will thereafter be selected with the same criterion and once all the feeders of Group`B’ are also exhausted, the cycle will be repeated for Groups A&B again.

viii)The sequencing of the feeders of each group will also be changed periodically to ensure that the same area is not affected repeatedly on subsequent days.

ix)	The advantages of the scheme are as follows

Automated operation

Control of duration of individual feeder outage time

Control of repetition of outage to the same area.

x)	The scheme is in the testing stage at present and quotations for relays have been sought from the OEMs.

xi)	On receipt of the same as well as the approval of GCC and DERC, the scheme will be implemented.  The expected time for completion is three months from date of the approval.

BYPL

As per directions from SLDC the load relief to be provided by BYPL system in case of flat system frequency dropping below threshold is as follows,

- When the frequency drops to 48.8 Hz  --  30 MW

- When the frequency drops to 48.6 Hz  --  40 MW

- When the frequency drops to 48.2 Hz  --  45 MW

The proposal for implementation of flat under frequency load relief scheme is as follows:

a) 	11 KV feeders feeding to important/strategic installations/areas like major hospitals, DJB, Rly station etc. shall be excluded from this scheme. All other 11 feeders emanating from BYPL Grids will be categorized into A & B groups depending on the level of non desirability to shed load as determined by various factors. The division will tentatively be in the ratio of 25% and 75% respectively.

b)	One set of under frequency relays will be installed at Balaji and I.G. Stadium grids (for redundancy), with PT supply inputs of Okhla and IP/Rajghat station supplies respectively. These relays shall be integrated with SCADA. The threshold on these relays shall be set as per above requirement and stage wise trip output command generated by relay shall be used by SCADA to provide desired relief.

c)	In case of operation of the relay due to any of the triggers, a specified number of feeders to obtain the desired relief shall be selected sequentially from Group A. The feeders which are already under outage or feeders which have been under outage at any point in the past 6 hours will be ignored at the time of selection.

d)	An automated group command will cause the actuation of the said scheme.

e)	In case of this condition persisting beyond a period of one hour, the next set of feeders will be shed while restoring supply to the earlier shed feeders.

f)	The scheme will continue in this fashion till all the available feeders in Group A are exhausted. The feeders of Group B will thereafter be selected with the same criterion and once all the feeders of Group B are also exhausted, the cycle will be repeated for Groups A & B again.

g)	The sequencing of the feeders of each group will also be changed periodically to ensure that the same area is not affected repeatedly on subsequent days.

The advantages of the scheme are as follows:

- Automated operation

- Control of duration of individual feeder outage time.

- Control of repetition of outage to the same area.

The scheme is in the testing stage at present and after getting approval of GCC and DERC the scheme will be implemented. The expected time for completion is three months from date of the approval.

NDPL

NDPL has indicated that the grouping of the feeders have been done to shed the load as per the quantum fixed by SLDC and the operation of same is mapped through SCADA system.  They have given the proof of operation of the Under Frequency Relays through SCADA system for the period 01.04.2010 upto 05.04.2010 as under :-

| Sr.No | Date | Grid | Type of Feeders shed | Nos. of feeders | Time | Freq. (Hz) | DTL | SCADA module | Quantum Load Shed (MW |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 1/4/10 | 220kV Subzi Mandi | 33kV Gulabi Bagh, 33kV Tripolia | 02 | 23:20:00 | 48.823 | Operated | Not Operated | 27 |
| 2 | 3/4/10 | 220kV Shalimar Bagh | 33kV SMB Khosla-2, 33kV Wazirpur-II Ckt-I | 02 | 18:25:00 | 48.819 | Operated | Not Operated | 33.25 |
| 3 | 3/4/10 | 220kV Rohini, 220kV Shalimar Bagh | 66kV Rohini-V Ckt-I& II 33kV SGT Nagar Ckt. 33kV Ranibagh Ckt-I& II | 04 | 19:05:00 | 48.84 | Operated | Not Operated | 70.85 |
| 4 | 3/4/10 | Azadpur, GTK, Ashok Vihar | Scheduled 11kV Feeders | 16 | 19:09:00 | 48.79 | Not Operated | Operated | 21 |
| 5 | 4/4/10 | 220kV Rohini, 220kV Shalimar Bagh | 66kV Rohini-V Ckt-I& II, 33kV SGT Nagar Ckt. 33kV Ranibagh Ckt-I & II | 05 | 08:46:00 | 48.8 | Operated | Operated | 51 |
| 6 | 4/4/10 | Azadpur, GTK | Scheduled 11kV feeders | 10 | 08:47:00 | 48.8 | Not Operated | Operated | 11.62 |
| 7 | 5/4/10 | 220kV Subzi Mandi | 33kV Tripolia Ckt, 33kV Gulabi Bagh Ckt. | 02 | 14:42:00 | 48.816 | Operated | Not Operated | 24 |
| 8 | 5/4/10 | 220kV Shalimar Bagh | 33kV Shalimar Bagh O/H Ckt-II 33kV Wazipur-II Ckt-I | 02 | 20:13:00 | 48.815 | Operated | Not Operated | 32 |
| 9 | 5/4/10 | 220kV Rohini | 66kV Rohini-VI Ckt-I& II | 05 | 23:05:00 | 48.815 | Operated | Not Operated | -- |

As the load shedding module effected by them through SCADA is satisfactorily functioning, to avoid duplicate operation of Under Frequency Relays through SCADA of NDPL and DTL sub-stations, they requested to lower the settings at 220kV Sub-Stations of DTL to 48.7Hz.

SLDC suggested that any lowering of settings without the successful testing and relief of required load shedding at each frequency level fixed by RPC would be detrimental to the stability to the System.  It also suggested the review of the scheme by the Protection Sub-Committee before taking any decision in this regard.

NDMC and MES

Due to the strategic important load to be catered by NDMC and MES these utilities are kept out of the ambit of normal under frequency relay load shedding scheme.

Concluding the discussions, Director (Operations) agreed the proposal of BSES utilities and advised go ahead for procurement of Under Frequency Relays and its operation through SCADA sensing. He advised DTL’s Protection Department also for implementation of Under Frequency Relays Load Shedding Scheme through SCADA sensing. He further advised the General Manager (O&M), DTL to look into the suggestion of NDPL for lowering the setting of Under frequency relays of the 1st stage i.e. from 48.8Hz to 48.7Hz. to avoid duplicacy of tripping from DTL S/stns and NDPL S/stns and to finalize the scheme after the full scrutiny by Protection Sub-committee and put for the approval of GCC within a fortnight time.

3	Accounting of Energy being generated from renewable energy sources.

In Delhi lot of non conventional energy sources is proposed to be added up to meet the statutory requirement of Renewal Purchase Obligation (RPO). The utilities requested SLDC to draw out accounting methodology for account for the energy generated from these sources.

NDPL indicated that they have commissioned three solar power generating stations in their areas and few projects are in process of installation and would be commissioned by next two to four months. Moreover some projects are also in the pipe line and will come in stream by end of 2010. Out of these Solar Power Projects, two projects are at DERC’s office and at CM’s residence.  These Non-Conventional sources have the capability of synchronization with the Grid.  The details of the projected already commissioned and proposed to be commissioned are as under :-

| List of Solar Projects taken up by NDPL as on 06.04.2010 |
| --- |
|  |  | Completed Projects |  |  |
| Sr. No | Capacity | Location | Actual/Proposed Date of Commissioning | Remarks |
| 1 | 3.96 KW | NDPL Corporate Office-Board Room | Sep-08 | Already Commissioned. |
| 2 | 14.85 KWp | NDPL Training Center-CENPEID,Rohini | Aug-08 | Already Commissioned. |
| 3 | 54 KWp | Pooth Khurd Grid, Bawana | March 2010 | Already Commissioned. |

|  |  | Ongoing Projects |  |  |
| --- | --- | --- | --- | --- |
| Sr. No | Capacity | Location | Actual / Proposed Date of Commissioning | Remarks |
| 1 | 1 MW | Keshav Puram | 31.03.2010 | Awarded to M/S Tata BP Solar India Ltd |
| 2 | 25 KW | Office of DERC | 31.03.2010 | Awarded to M/S Tata BP Solar India Ltd |
| 3 | 25 KW | Office residence of CM | 31.03.2010 | Awarded to M/S Tata BP Solar India Ltd |
| 4 | 43 KW | A-7 Grid Narela | 30.06.2010 | NIT to be Floated shortly |
| Future Projects in Pipeline |
| 1 | 100 MW | Rajasthan | In phases starting from 2011 onwards | 500 Acres of Land Identified. Pursuing with Rajasthan Government for Land Allocation. |
| 2 | 100 MW | NDPL Area | 2 to 3 years Horizon | Roof Top Solar Generation - Turn consumers into Generators and add another 100 MWp (5 kWp @ 20000 consumers) |
| 3 | 2500-3000KW | NDPL Area | 30.06.2010 | Solar Power on Rooftops of all Grid Substations |
| 4 | 360KW | NDPL Area | 30.06.2010 | Rooftop of NDPL Housing Colonies at Narela & Shalimar Bagh |
| 5 | 1.5 KWp | NDPL Area | 30.04.2010 | Solar Traffic Light at Madhuban Chowk. NOC obtained from Delhi Traffic Police. Shall be Commissioned by due date subject to issuance of NOC from PWD. |

NDPL representative further indicated that the scheduling & Energy Accounting of the power to be generated from these Solar Power Stations or from any other resources is to be done as per ABT guide lines and frame work of Non-conventional power plants issued by CERC/MNRE. The Clause 86(1) (e) of Electricity Act 2003 also mandates

“

(e) promote co-generation and generation of electricity from renewable sources of energy by providing suitable measures for connectivity with the grid and sale of electricity to any person, and also specify, for purchase of electricity from such sources, a percentage of the total consumption of electricity in the area of a distribution licensee;”

It was also mentioned that DERC has advised the Distribution Licensees to have atleast 1% RPO (Renewal Power Obligation) in line with the above statutory provision of the Act. In view of above, the promotion of the availability of such sources should be done.

In the last Commercial Sub-Committee meeting, the matter has come up for discussions and SLDC’s view points were as under for accounting of energy generated from renewable energy sources:-

- In case, non conventional energy sources installed by a distribution utility in other distribution utility’s area, the energy made available in 15 minutes time block would be adjusted as energy availability from the sources to the distribution licensees.  The same quantum of energy would be added to the energy from the distribution licensee in whose area, the plants have installed to arrive the drawal of the utility from the Grid.

These adjustments would be done on post facto basis.

- In case, the non conventional sources are installed by the distribution utility in its own area, no adjustment would be done.  However, SLDC shall indicate the availability of power from such sources in its monthly accounts once the UI accounts for the entire month are issued.

Now NDPL requested to adopt the methodology in view of the fast process of commissioning of Non-Conventional Grid Connected Solar PV Units.

NDMC also indicated that it is procuring 3.6MW power to be generated by PWD, GNCTD through Solar Energy Plant and CNG based Turbine.  These plants are likely to be commissioned at the Netball Stadium, Tyagraj Nagar, New Delhi.  They also requested the accounting of the these energy sources as the generation from the sources is going to be injected in BSES areas and the accounting should be done against NDMC.

After detailed discussions, the following has been finalized :

- ABT Meters at generation points will be installed by the Distribution utility, installing the Renewable energy sources. The meters shall be jointly tested and sealed by DTL and the utility.

- Metering Deptt. of DTL will download the data from these meters weekly as being done for all other boundary meters and downloaded data will be provided to SLDC.

- Since, as per CERC Regulations, all the renewable energy power plants are ‘MUST RUN” plants, the scheduling is to be done on post facto basis as per the actual generation.

- No transmission losses or transmission charges will be applicable and actual ex-bus generation will be considered as schedule and actual energy.

v)	Energy accounting of Renewable Energy shall be done as under :

- Generating Station is installed by the distribution utility in its own area -  Energy generated from these plants will not be considered in the UI Bill calculation. However, SLDC will indicate the energy generated from these sources in the monthly State Energy Account as per the downloaded data of DTL, once the data of entire month is received.

- Generating Station is installed by the distribution utility in other distribution utility’s area – The energy made available in 15 minutes time block would be adjusted as energy available to the distribution utility from these sources and accordingly added in the scheduled energy. The same quantum of energy would be added to the actual energy of the distribution utility, in whose area the plant have installed, to arrive the drawl of the utility from the grid. This schedule and actual energy will be considered in the UI Bill accounting.

These adjustments would be done on post facto basis.

The above mentioned procedure is applicable only for the renewable energy generating sources installed by the distribution utilities or renewable energy purchased by distribution utility from third party and not for the ‘Roof Top Solar Plants’ to be installed by the consumers.

With regard to power supply from the conventional source i.e. Gas Turbine since the accounting methodology of Renewable Energy Sources can not be applied.  NDMC was advised to approach Planning Department of DTL for getting the Open Access as the power should flow through Open Access route.   However, for energy accounting for renewable energy sources can be done on the above mentioned methods.

3. 	Power arrangement for summer season.

SLDC indicated that so far Delhi’s power supply position has been by and large satisfactory. Delhi as a whole is also under drawing further grid. However, same Distribution Licensees over draw while others under draw. The under drawing utilities intend to sell power out side Delhi causing overdrawal by Delhi in some slots. Director (Operations) advised all Distribution Licensees to evolve a method to divert one Discom’s surplus to meet the short fall of other Discom to some extent as was done in last year by Delhi Power Procurement Group (DPPG) immediately so that power selling by Delhi would be done only if Delhi as a whole is having surplus. All stake holders agreed the proposal.

Annexure-1

The list of the officers attended the meeting held at SLDC on 06.04.2010 at 11.00hrs. with regard to installation of additional capacitors, Under frequency relay installations at Discoms, Accounting of Energy from non-conventional energy sources etc.

| Name | Designation | Utility | Mobile no. |
| --- | --- | --- | --- |
| Sh. A.K. Kaul | Director (Operations), -in Chair | DTL | 9810299692 |
| Sh. Roop Kumar | G. M. (SLDC) | SLDC | 9540040629 |
| Sh. Raj Bhartiya | G. M. (Plg) | DTL | 9540040609 |
| Sh. Nirmaljit Singh | G. M. (Comml.) | DTL | 9540040622 |
| Sh. Bhupinder Nath | G. M. (O&M) | DTL | 9540040627 |
| Sh. Ved Mitra | DGM(Plg) | DTL | 9540040632 |
| Sh. V. Venugopal | DGM(System Operation) | SLDC | 9871093902 |
| Sh. V. K. Garg | DGM(Comml.) | DTL | 9540040634 |
| Sh. Hitesh Kumar | Manager (ICM) | DTL | 9540040662 |
| Sh. Sanjeev Kumar | AM(T), SO | SLDC | 9540040917 |
| Sh. Deepak Sharma | JE(E), SO-EA | SLDC | 9540041008 |
| Sh. Deepak Sachdeva | EE(E) | NDMC | 9811120675 |
| Sh. Madan Pal | AEE(Power) | NDMC | 9968267933 |
| Sh. Sanjay Kr. Gupta |  | NDMC | 9953745323 |
| Sh. A. W. Ansari | AEE | NDMC | 9910391769 |
| Sh. M. C. Sharma | Advisor | BRPL | 9312147003 |
| Sh. K. Sheshadri | AVP | BRPL | 9350261134 |
| Sh. Ajay Kumar | Addl. VP | BRPL | 9350683910 |
| Sh. Manoj Kumar |  | BYPL | 9312782575 |
| Sh. Ram Sahai |  | BYPL | 9350110204 |
| Sh. A. K. Sharma | HeaD EHV | BYPL | 9350130391 |
| Sh. Ashish Kr. Dutta | Manager | NDPL | 9871798566 |
| Sh. Jay Shankar Tiwary | Sr. Mgr | NDPL | 9871798540 |
| Sh. Arunabha Basu | Vice President | NDPL | 9818100576 |
| Sh. Sugata M. |  | NDPL | 9971395275 |
| Sh. Vineet Taneja |  | NDPL | 9810378852 |
| Sh. S. Samantha |  | NDPL | 9971122431 |