## NDPL
DELHI TRANSCO LIMITED | [15 empty] | DECEMBER-2013
REACTIVE ENERGY CONSUMPTION STATEMENT
Customer:NORTH DELHI POWER LIMITED.
NDPL(+) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
GOPAL PUR
1 | Tx.1 | 4864925 | ELSTER | Kvarh(Lead/Lag) | -1000 | 993693 | 994928 | -1235 | 1235000 | 1.235 | 999254 | 999254 | 0 | 0 | 0
2 | TX.2 | 5128432 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997758 | 998394 | -636 | 636000 | 0.636 | 998273 | 998274 | -1 | 1000 | 0.001
3 | Tx.3 | 4864905 | ELSTER | Kvarh(Lead/Lag) | -1000 | 9070 | 10481 | -1411 | 1411000 | 1.411 | 996281 | 996281 | 0 | 0 | 0
SUBZI MANDI
4 | Tx.1 | 4864912 | ELSTER | Kvarh(Lead/Lag) | -1000 | 974560 | 975073 | -513 | 513000 | 0.513 | 976185 | 976185 | 0 | 0 | 0
5 | Tx.2 | 4864913 | ELSTER | Kvarh(Lead/Lag) | -1000 | 918203 | 918730 | -527 | 527000 | 0.527 | 941052 | 941078 | -26 | 26000 | 0.026
ROHINI
6 | Tx.1 | 4864982 | ELSTER | Kvarh(Lead/Lag) | -1000 | 20428 | 19506 | 922 | -922000 | -0.922 | 17170 | 17166 | 4 | -4000 | -0.004
7 | Tx.2 | 4864983 | ELSTER | Kvarh(Lead/Lag) | -1000 | 16976 | 17708 | -732 | 732000 | 0.732 | 13097 | 13102 | -5 | 5000 | 0.005
8 | Tx.-3 | 4864953 | ELSTER | Kvarh(Lead/Lag) | -1250 | 15695 | 16043 | -348 | 435000 | 0.435 | 995461 | 995465 | -4 | 5000 | 0.005
9 | Tx.-4 | 4864984 | ELSTER | Kvarh(Lead/Lag) | -1000 | 10455 | 11259 | -804 | 804000 | 0.804 | 985266 | 985268 | -2 | 2000 | 0.002
SHALIMAR BAGH
10 | Tx.1 | 4864939 | ELSTER | Kvarh(Lead/Lag) | -1000 | 31173 | 31019 | 154 | -154000 | -0.154 | 9098 | 9097 | 1 | -1000 | -0.001
11 | Tx.-2 | 4864940 | ELSTER | Kvarh(Lead/Lag) | -1000 | 994596 | 995100 | -504 | 504000 | 0.504 | 3866 | 3866 | 0 | 0 | 0
12 | Tx.-3 | 5128410 | ELSTER | Kvarh(Lead/Lag) | -1000 | 995430 | 996000 | -570 | 570000 | 0.57 | 999329 | 999329 | 0 | 0 | 0
13 | 220KV DMRC | 4865060 | ELSTER | Kvarh(Lead/Lag) | 1000 | 915214 | 915695 | -481 | -481000 | -0.481 | 920513 | 920513 | 0 | 0 | 0
NARELA
14 | Tx.1 | 4865034 | ELSTER | Kvarh(Lead/Lag) | -1000 | 992564 | 993440 | -876 | 876000 | 0.876 | 16927 | 16927 | 0 | 0 | 0
15 | Tx.2 | 4865035 | ELSTER | Kvarh(Lead/Lag) | -1000 | 230 | 383 | -153 | 153000 | 0.153 | 19649 | 19649 | 0 | 0 | 0
16 | Tx.3 | 4865052 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1098 | 744 | 354 | -354000 | -0.354 | 999938 | 999938 | 0 | 0 | 0
NARAINA
17 | O/G REWARI LINE 1 | 4864800 | ELSTER | Kvarh(Lead/Lag) | 200 | 999836 | 999990 | -154 | -30800 | -0.0308 | 993174 | 993169 | 5 | 1000 | 0.001
18 | O/G REWARI LINE 2 | 4864887 | ELSTER | Kvarh(Lead/Lag) | 1000 | 352 | 307 | 45 | 45000 | 0.045 | 29306 | 29304 | 2 | 2000 | 0.002
19 | 16 MVA TX.-1 | 4864798 | ELSTER | Kvarh(Lead/Lag) | 100 | 2672 | 2535 | 137 | 13700 | 0.0137 | 154878 | 154875 | 3 | 300 | 0.0003
20 | 16 MVA TX.-2 | 4864799 | ELSTER | Kvarh(Lead/Lag) | 100 | 9154 | 7141 | 2013 | 201300 | 0.2013 | 229711 | 228980 | 731 | 73100 | 0.0731
21 | INDER PURI | 4864888 | ELSTER | Kvarh(Lead/Lag) | 1000 | 996128 | 996139 | -11 | -11000 | -0.011 | 3942 | 3978 | -36 | -36000 | -0.036
22 | INDER PURI-2 | 5128402 | ELSTER | Kvarh(Lead/Lag) | 1000 | 41 | 19 | 22 | 22000 | 0.022 | 8153 | 8163 | -10 | -10000 | -0.01
KASHMIRI GATE
23 | 221 kV DMRC #1 | 4865057 | ELSTER | Kvarh(Lead/Lag) | 1000 | 644515 | 645873 | -1358 | -1358000 | -1.358 | 798972 | 798973 | -1 | -1000 | -0.001
24 | 221 kV DMRC #2 | 4865058 | ELSTER | Kvarh(Lead/Lag) | 1000 | 652027 | 653273 | -1246 | -1246000 | -1.246 | 832151 | 832153 | -2 | -2000 | -0.002
25 | CIVIL LINE | 4864902 | ELSTER | Kvarh(Lead/Lag) | 400 | 448 | 32 | 416 | 166400 | 0.1664 | 0 | 0 | 0 | 0 | 0
26 | CIVIL LINE-2 | 5128405 | ELSTER | Kvarh(Lead/Lag) | 500 | 1838 | 1571 | 267 | 133500 | 0.1335 | 2047 | 2036 | 11 | 5500 | 0.0055
KANJAWALA
27 | TX-1 | 4865054 | ELSTER | Kvarh(Lead/Lag) | -1000 | 14683 | 14379 | 304 | -304000 | -0.304 | 981888 | 981889 | -1 | 1000 | 0.001
28 | Tx.2 | 4865036 | ELSTER | Kvarh(Lead/Lag) | -1000 | 3169 | 2129 | 1040 | -1040000 | -1.04 | 999834 | 999835 | -1 | 1000 | 0.001
BAWANA
29 | I/C 100 MVA PR.TR. | 4865056 | ELSTER | Kvarh(Lead/Lag) | -1000 | 993549 | 993211 | 338 | -338000 | -0.338 | 925950 | 926159 | -209 | 209000 | 0.209
DSIDC BAWANA
30 | 66KV TX.2 | 4865049 | ELSTER | Kvarh(Lead/Lag) | -1000 | 2109 | 1649 | 460 | -460000 | -0.46 | 999908 | 999908 | 0 | 0 | 0
31 | 66KV TX.3 | 4865022 | ELSTER | Kvarh(Lead/Lag) | -1000 | 48569 | 45081 | 3488 | -3488000 | -3.488 | 999926 | 999928 | -2 | 2000 | 0.002
ROHINI-II
32 | Tx.1 | 5128463 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999722 | 999722 | 0 | 0 | 0 | 999999 | 999999 | 0 | 0 | 0
33 | Tx.2 | 5128456 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999792 | 999378 | 414 | -414000 | -0.414 | 0 | 0 | 0 | 0 | 0 | Reverse Polarity & time mismatch corrected on 19/12/13
| Tx.2 | 5128456 | ELSTER | Kvarh(Lead/Lag) | -1000 |  |  |  |  | -0.57323 |  |  |  |  | 0 | Assessment from 01/12/13 to 19/12/13(Time Mismatch)
EXPORT TO EAST & CENTRE IMPORTS
SHASTRI PARK
34 | PUSA GRID-I | 4864843 | ELSTER | Kvarh(Lead/Lag) | 1000 | 1564 | 1539 | 25 | 25000 | 0.025 | 21101 | 21080 | 21 | 21000 | 0.021
35 | PUSA GRID-II | 4864844 | ELSTER | Kvarh(Lead/Lag) | 1000 | 269 | 303 | -34 | -34000 | -0.034 | 2013 | 2027 | -14 | -14000 | -0.014
| NDPL(+) continue | [14 empty] | DECEMBER-2013
DMS
36 | 33KV PANDAV NGR | 4865169 | ELSTER | Kvarh(Lead/Lag) | 1000 | 1194 | 1230 | -36 | -36000 | -0.036 | 60903 | 60903 | 0 | 0 | 0
REWARI LINE
37 | 20MVA Tx-2 | 4864824 | ELSTER | Kvarh(Lead/Lag) | 100 | 804 | 804 | 0 | 0 | 0 | 77729 | 77721 | 8 | 800 | 0.0008
VISHAL
38 | RAMESH NAGAR-1 | 4865090 | ELSTER | Kvarh(Lead/Lag) | 100 | 9213 | 9217 | -4 | -400 | -0.0004 | 28708 | 28824 | -116 | -11600 | -0.0116
39 | BALI NAGAR -1 | 4902519 | ELSTER | Kvarh(Lead/Lag) | 100 | 10525 | 10530 | -5 | -500 | -0.0005 | 51109 | 51144 | -35 | -3500 | -0.0035
40 | ESI HOSPITAL | 4902520 | ELSTER | Kvarh(Lead/Lag) | 100 | 15813 | 15718 | 95 | 9500 | 0.0095 | 53799 | 53261 | 538 | 53800 | 0.0538
S.B.MILL
41 | MOTI NAGAR KIOSK | 4902521 | ELSTER | Kvarh(Lead/Lag) | 100 | 42428 | 42213 | 215 | 21500 | 0.0215 | 17222 | 16639 | 583 | 58300 | 0.0583
42 | 53 RAMA ROAD | 4902522 | ELSTER | Kvarh(Lead/Lag) | 100 | 840 | 840 | 0 | 0 | 0 | 185 | 185 | 0 | 0 | 0
43 | BREAK FAST | 4902523 | ELSTER | Kvarh(Lead/Lag) | 100 | 999815 | 999815 | 0 | 0 | 0 | 999943 | 999943 | 0 | 0 | 0
44 | 70 RAMA ROAD | 4902524 | ELSTER | Kvarh(Lead/Lag) | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | MOTI NAGAR 2 | 4902605 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | NAJAFGARH ROAD | 4902526 | ELSTER | Kvarh(Lead/Lag) | 100 | 16873 | 16862 | 11 | 1100 | 0.0011 | 15236 | 14755 | 481 | 48100 | 0.0481
47 | PHILIPS | 4902529 | ELSTER | Kvarh(Lead/Lag) | 44.44 | 999086 | 999372 | -286 | -12709.84 | -0.01271 | 587 | 761 | -174 | -7732.56 | -0.0077326
B.G.ROAD
48 | CSA | 4865091 | ELSTER | Kvarh(Lead/Lag) | 500 | 5452 | 5393 | 59 | 29500 | 0.0295 | 28792 | 28716 | 76 | 38000 | 0.038
49 | DCM NO.1 | 4902530 | ELSTER | Kvarh(Lead/Lag) | 500 | 3601 | 3556 | 45 | 22500 | 0.0225 | 26659 | 26616 | 43 | 21500 | 0.0215
50 | DCM NO.2 | 4902531 | ELSTER | Kvarh(Lead/Lag) | 500 | 5206 | 5121 | 85 | 42500 | 0.0425 | 14551 | 14543 | 8 | 4000 | 0.004
51 | SADAR S/S | 4865072 | ELSTER | Kvarh(Lead/Lag) | 666.6667 | 566 | 514 | 52 | 34666.6667 | 0.034667 | 554 | 546 | 8 | 5333.3333 | 0.0053333
D.M.S.
52 | PHILIPS | 4902535 | ELSTER | Kvarh(Lead/Lag) | 100 | 993917 | 994664 | -747 | -74700 | -0.0747 | 5898 | 5898 | 0 | 0 | 0
53 | 69 NG ROAD | 4902536 | ELSTER | Kvarh(Lead/Lag) | 100 | 7991 | 8046 | -55 | -5500 | -0.0055 | 15336 | 15336 | 0 | 0 | 0
54 | J BLOCK KIRTI NGR | 4902537 | ELSTER | Kvarh(Lead/Lag) | 100 | 22445 | 21664 | 781 | 78100 | 0.0781 | 54105 | 54092 | 13 | 1300 | 0.0013
55 | H BLOCK | 4902579 | ELSTER | Kvarh(Lead/Lag) | 100 | 4695 | 4748 | -53 | -5300 | -0.0053 | 999974 | 999975 | -1 | -100 | -0.0001
56 | SHADI KHAM PUR | 4902539 | ELSTER | Kvarh(Lead/Lag) | 100 | 998783 | 998810 | -27 | -2700 | -0.0027 | 131 | 131 | 0 | 0 | 0
57 | BREAK FAST | 4902540 | ELSTER | Kvarh(Lead/Lag) | 100 | 15 | 15 | 0 | 0 | 0 | 13398 | 13398 | 0 | 0 | 0
FAIZ ROAD
58 | TIBIA COLLEGE-1 | 4902541 | ELSTER | Kvarh(Lead/Lag) | 100 | 17398 | 16890 | 508 | 50800 | 0.0508 | 71878 | 71877 | 1 | 100 | 0.0001
59 | TIBIA COLLEGE-2 | 4902542 | ELSTER | Kvarh(Lead/Lag) | 100 | 12965 | 12610 | 355 | 35500 | 0.0355 | 62674 | 62590 | 84 | 8400 | 0.0084
60 | MANAK PURA | 4902543 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  |  |  | 0.083133 |  |  |  |  | 0 | Assessment (Meter faulty)
KASHMIRI GATE
61 | 20MVA TX. | 4864807 | ELSTER | Kvarh(Lead/Lag) | 100 | 138816 | 135809 | 3007 | 300700 | 0.3007 | 23963 | 23936 | 27 | 2700 | 0.0027
62 | FLYOVER | 4865086 | ELSTER | Kvarh(Lead/Lag) | 100 | 21001 | 20688 | 313 | 31300 | 0.0313 | 41325 | 41312 | 13 | 1300 | 0.0013
63 | B/C (IMP. TO NDPL) | 4902571 | ELSTER | Kvarh(Lead/Lag) | -300 | 23 | 23 | 0 | 0 | 0 | 65 | 65 | 0 | 0 | 0
REWARI LINE (11KV TRANSFER OF ENERGY)
64 | BSES -NDPL(EX.) ON BUS-1&2 | 4902577 | ELSTER | Kvarh(Lead/Lag) | -400 | 995589 | 995589 | 0 | 0 | 0 | 36 | 36 | 0 | 0 | 0
65 | BSES -NDPL(EX.) ON BUS-2&3 | 4902516 | ELSTER | Kvarh(Lead/Lag) | 100 | 999273 | 999273 | 0 | 0 | 0 | 999398 | 999398 | 0 | 0 | 0
Mundka
66 | 66KV MANGOL PURI | 5128444 | ELSTER | Kvarh(Lead/Lag) | 800 | 994101 | 994101 | 0 | 0 | 0 | 344 | 344 | 0 | 0 | 0
67 | GHEWARA | 5100232 | ELSTER | Kvarh(Lead/Lag) | 800 | 991539 | 992627 | -1088 | -870400 | -0.8704 | 999987 | 999987 | 0 | 0 | 0
| ENERGY INPUT AT 66/33/11 KV LEVEL | [8 empty] | -2.4725 |  |  |  |  | 0.5076
NDPL(-) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 % |  |  | DECEMBER-2013
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
NARAINA
1 | GOPI NATH BAZAAR | 4865092 | ELSTER | Kvarh(Lead/Lag) | -100 | 14265 | 13861 | 404 | -40400 | -0.0404 | 14243 | 14070 | 173 | -17300 | -0.0173
MANGOLPURI
2 | NANGLOI-2 EXP | 4864955 | ELSTER | Kvarh(Lead/Lag) | -1000 | 9095 | 8717 | 378 | -378000 | -0.378 | 7061 | 7047 | 14 | -14000 | -0.014
SUBZI MANDI
3 | O/G BG Rd.1 | 4864808 | ELSTER | Kvarh(Lead/Lag) | -200 | 4288 | 3962 | 326 | -65200 | -0.0652 | 11880 | 11798 | 82 | -16400 | -0.0164
4 | O/G BG Rd.2 | 4864841 | ELSTER | Kvarh(Lead/Lag) | -1000 | 14930 | 14713 | 217 | -217000 | -0.217 | 31680 | 31646 | 34 | -34000 | -0.034
SUDARSHAN PARK
5 | VISHAL (EXP) | 4864898 | ELSTER | Kvarh(Lead/Lag) | -100 | 11533 | 11735 | -202 | 20200 | 0.0202 | 61483 | 61487 | -4 | 400 | 0.0004
REWARI LINE (ENERGY EXCHANGE WITH NDPL)
6 | 33KV B/C | 4865174 | ELSTER | Kvarh(Lead/Lag) | -1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KANJAWALA
7 | 66KV DMRC | 4864961 | ELSTER | Kvarh(Lead/Lag) | -1000 | 949018 | 950752 | -1734 | 1734000 | 1.734 | 992454 | 992454 | 0 | 0 | 0
MUNDKA
8 | 66KV NGL. T-OFF MGL P | 5128407 | ELSTER | Kvarh(Lead/Lag) | 2000 | 999423 | 999423 | 0 | 0 | 0 | 999980 | 999980 | 0 | 0 | 0
| TOTAL OF INTER COMPANY EXCHANGE POINTS | [8 empty] | 1.0536 |  |  |  |  | -0.0813
EXECUTIVE SUMMERY N.D.P.L.
1) ENERGY RELEASED AT 66/33/11 KV LEVEL (Refer sheet NDPL(+)) | [9 empty] | -2.4725 |  |  |  |  | 0.5076
2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer sheet NDPL(-)) | [9 empty] | 1.0536 |  |  |  |  | -0.0813
3) FROM ROHTAK ROAD (REFER ENERGY BALANCE SHEET ROHTAK ROAD ENCL) | [9 empty] | 1.3962 |  |  |  |  | -0.10903
NET ENERGY TO NORTH DELHI POWER LIMITED | [9 empty] | -0.022753 |  |  |  |  | 0.31728
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | -0.022753 | (REACTIVE MUs) |  |  |  | 0.31728 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | 0.2774 | (REACTIVE MUs) |  |  |  | -2.4014 | (REACTIVE MUs)
[9 empty] | TOTAL | 0.25465 | (REACTIVE MUs) |  |  |  | -2.0841 | (REACTIVE MUs)

## BYPL
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [15 empty] | DECEMBER-2013
Customer:BSES YAMUNA POWER LIMITED.
BYPL(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
I.P.STATION 33KV FEEDER
1 | KAMLA MKT.-B-18 | 4865098 | ELSTER | Kvarh(Lead/Lag) | 100 | 999998 | 999998 | 0 | 0 | 0 | 37956 | 37956 | 0 | 0 | 0
2 | KAMLA MKT.B-30 | 4865161 | ELSTER | Kvarh(Lead/Lag) | 100 | 989960 | 989268 | 692 | 69200 | 0.0692 | 69352 | 68107 | 1245 | 124500 | 0.1245
3 | P. HOSPITAL BAY-19 | 4865099 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  |  |  | -0.0056 |  |  |  |  | -0.0017 | Metering not in order
4 | IG STD- BAY-29 | 4865162 | ELSTER | Kvarh(Lead/Lag) | 100 | 19295 | 19180 | 115 | 11500 | 0.0115 | 23881 | 23722 | 159 | 15900 | 0.0159
5 | IG STD-BAY 31 | 4865103 | ELSTER | Kvarh(Lead/Lag) | 100 | 4039 | 5086 | -1047 | -104700 | -0.1047 | 4591 | 4685 | -94 | -9400 | -0.0094
6 | DELHI GATE B-17 | 4865101 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  |  |  | 0.0005 |  |  |  |  | 0.2978 | Metering not in order
7 | MINTO RD. B-34 | 4865102 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  |  |  | -0.0058 |  |  |  |  | -0.07 | Metering not in order
RPH
8 | KAMLA MKT.-2 | 4864884 | ELSTER | Kvarh(Lead/Lag) | 1000 | 995884 | 996288 | -404 | -404000 | -0.404 | 835 | 834 | 1 | 1000 | 0.001
9 | FOUNTAIN BAY-16 | 4864831 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999474 | 999601 | -127 | -127000 | -0.127 | 1942 | 1934 | 8 | 8000 | 0.008
10 | MINTO RD BAY-17 | 4864832 | ELSTER | Kvarh(Lead/Lag) | 1000 | 1154 | 930 | 224 | 224000 | 0.224 | 1326 | 1291 | 35 | 35000 | 0.035
11 | TOWN HALL-3 | 4864833 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999600 | 999677 | -77 | -77000 | -0.077 | 2737 | 2732 | 5 | 5000 | 0.005
12 | LAHORI GATE-1 | 4864834 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999180 | 999252 | -72 | -72000 | -0.072 | 4093 | 4091 | 2 | 2000 | 0.002
13 | LAHORI GATE-2 | 4864835 | ELSTER | Kvarh(Lead/Lag) | 1000 | 617 | 747 | -130 | -130000 | -0.13 | 1074 | 1035 | 39 | 39000 | 0.039
14 | JAMA MASJID-1 | 4864836 | ELSTER | Kvarh(Lead/Lag) | 1000 | 101 | 150 | -49 | -49000 | -0.049 | 16515 | 16514 | 1 | 1000 | 0.001
15 | JAMA MASJID-2 | 4864837 | ELSTER | Kvarh(Lead/Lag) | 1000 | 927 | 732 | 195 | 195000 | 0.195 | 37106 | 37091 | 15 | 15000 | 0.015
16 | GB PANTH(Bay-13) | 4864838 | ELSTER | Kvarh(Lead/Lag) | 1000 | 259 | 259 | 0 | 0 | 0 | 24566 | 24525 | 41 | 41000 | 0.041
17 | SACHV. (Bay-12) | 4864839 | ELSTER | Kvarh(Lead/Lag) | 1000 | 1009 | 839 | 170 | 170000 | 0.17 | 8377 | 8353 | 24 | 24000 | 0.024
18 | 6.6 KV IRRG.PUMP | 4864788 | ELSTER | Kvarh(Lead/Lag) | 100 | 1704 | 1552 | 152 | 15200 | 0.0152 | 1 | 1 | 0 | 0 | 0
19 | KAMLA MKT. (B-19) | 4864883 | ELSTER | Kvarh(Lead/Lag) | 1000 | 998402 | 998542 | -140 | -140000 | -0.14 | 12589 | 12518 | 71 | 71000 | 0.071
GT
20 | DMRC. CKT.-I | 4865041 | ELSTER | Kvarh(Lead/Lag) | 1100 | 999998 | 999998 | 0 | 0 | 0 | 754275 | 758269 | -3994 | -4393400 | -4.3934
21 | DMRC CKT.-II | 4865042 | ELSTER | Kvarh(Lead/Lag) | 1100 | 999998 | 999998 | 0 | 0 | 0 | 796714 | 800954 | -4240 | -4664000 | -4.664
22 | AKSHARDHAM | 4864943 | ELSTER | Kvarh(Lead/Lag) | 1000 | 988438 | 988757 | -319 | -319000 | -0.319 | 9052 | 9094 | -42 | -42000 | -0.042
| KASHMIRI GATE | [8 empty] | -0.7138 |  |  |  |  | -8.8574
23 | 100 MVA TX.-1 | 4864910 | ELSTER | Kvarh(Lead/Lag) | -1000 | 960646 | 961233 | -587 | 587000 | 0.587 | 966221 | 966255 | -34 | 34000 | 0.034
24 | 100 MVA TX.-2 | 4864911 | ELSTER | Kvarh(Lead/Lag) | -1000 | 972916 | 974049 | -1133 | 1133000 | 1.133 | 962283 | 962296 | -13 | 13000 | 0.013
25 | B/C (IMP. TO BYPL) | 4902571 | ELSTER | Kvarh(Lead/Lag) | 300 | 23 | 23 | 0 | 0 | 0 | 65 | 65 | 0 | 0 | 0
NARAINA
26 | DMS | 5128409 | ELSTER | Kvarh(Lead/Lag) | 1000 | 87 | 107 | -20 | -20000 | -0.02 | 3540 | 3490 | 50 | 50000 | 0.05
PARK STREET
27 | TX.-1 (66KV) | 4864962 | ELSTER | Kvarh(Lead/Lag) | -1000 | 36381 | 31494 | 4887 | -4887000 | -4.887 | 972932 | 972932 | 0 | 0 | 0
28 | TX.-2(66KV) | 4865033 | ELSTER | Kvarh(Lead/Lag) | -1000 | 16400 | 14576 | 1824 | -1824000 | -1.824 | 967895 | 968043 | -148 | 148000 | 0.148
29 | TX.-1(33KV) | 5128420 | ELSTER | Kvarh(Lead/Lag) | -1000 | 996996 | 997346 | -350 | 350000 | 0.35 | 996415 | 996415 | 0 | 0 | 0
30 | TX.-2(33KV) | 4864935 | ELSTER | Kvarh(Lead/Lag) | -1000 | 980251 | 981283 | -1032 | 1032000 | 1.032 | 992299 | 992299 | 0 | 0 | 0
IMPORTS
SUBZI MANDI
31 | O/G BG Rd.1 | 4864808 | ELSTER | Kvarh(Lead/Lag) | 200 | 4288 | 3962 | 326 | 65200 | 0.0652 | 11880 | 11798 | 82 | 16400 | 0.0164
32 | O/G BG Rd.2 | 4864841 | ELSTER | Kvarh(Lead/Lag) | 1000 | 14930 | 14713 | 217 | 217000 | 0.217 | 31680 | 31646 | 34 | 34000 | 0.034
RIDGE VALLEY
33 | O/G SHANKAR RD.1 | 4865134 | ELSTER | Kvarh(Lead/Lag) | 100 | 111280 | 110284 | 996 | 99600 | 0.0996 | 1617 | 1617 | 0 | 0 | 0
34 | O/G SHANKAR RD.2 | 4865135 | ELSTER | Kvarh(Lead/Lag) | 100 | 105385 | 103629 | 1756 | 175600 | 0.1756 | 2383 | 2383 | 0 | 0 | 0
| ENERGY INPUT AT 66/33KK LEVEL | [8 empty] | -3.8203 |  |  |  |  | -8.2049
| (A) NET ENERGY TO CENTRAL | [8 empty] | -3.8203 |  |  |  |  | -8.2049
DECEMBER-2013
BYPL(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
S.O.W.
1 | Tx.1 | 4864968 | ELSTER | Kvarh(Lead/Lag) | -1000 | 993757 | 994114 | -357 | 357000 | 0.357 | 917856 | 918012 | -156 | 156000 | 0.156
2 | Tx.2 | 4864980 | ELSTER | Kvarh(Lead/Lag) | -1000 | 13625 | 13721 | -96 | 96000 | 0.096 | 937709 | 937892 | -183 | 183000 | 0.183
3 | Tx.3 | 5128436 | ELSTER | Kvarh(Lead/Lag) | -1000 | 995562 | 996133 | -571 | 571000 | 0.571 | 981903 | 982043 | -140 | 140000 | 0.14
PPG
4 | Tx.1 (66 KV) | 4864915 | ELSTER | Kvarh(Lead/Lag) | -1000 | 913335 | 915348 | -2013 | 2013000 | 2.013 | 992037 | 992037 | 0 | 0 | 0
5 | Tx.2 (66 KV) | 4864993 | ELSTER | Kvarh(Lead/Lag) | -1000 | 902876 | 905171 | -2295 | 2295000 | 2.295 | 990458 | 990458 | 0 | 0 | 0
6 | 100 MVA Tx.1 (33 KV) | 4864914 | ELSTER | Kvarh(Lead/Lag) | -1000 | 3279 | 2459 | 820 | -820000 | -0.82 | 992192 | 992180 | 12 | -12000 | -0.012
7 | 50 MVA Tx.-2 (33 KV) | 4865167 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1655 | 1655 | 0 | 0 | 0 | 980809 | 980809 | 0 | 0 | 0
8 | 50MVA Tx.3 (33 KV) | 4864893 | ELSTER | Kvarh(Lead/Lag) | -2000 | 999009 | 998808 | 201 | -402000 | -0.402 | 985600 | 985703 | -103 | 206000 | 0.206
9 | 100MVA Tx.4 (33 KV) | 4864918 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999928 | 999705 | 223 | -223000 | -0.223 | 963309 | 963424 | -115 | 115000 | 0.115
GEETA COLONY
10 | I/C-I | 4864916 | ELSTER | Kvarh(Lead/Lag) | -1000 | 4809 | 5828 | -1019 | 1019000 | 1.019 | 914639 | 914771 | -132 | 132000 | 0.132
11 | I/C-II | 4864917 | ELSTER | Kvarh(Lead/Lag) | -1000 | 963108 | 963909 | -801 | 801000 | 0.801 | 870828 | 870927 | -99 | 99000 | 0.099
GAZIPUR
12 | TX.-1 | 4865053 | ELSTER | Kvarh(Lead/Lag) | -1000 | 20586 | 21760 | -1174 | 1174000 | 1.174 | 34073 | 34073 | 0 | 0 | 0
13 | TX-2 | 4864986 | ELSTER | Kvarh(Lead/Lag) | -1000 | 20529 | 20936 | -407 | 407000 | 0.407 | 43771 | 43782 | -11 | 11000 | 0.011
SB MILL
14 | ZAKHIRA | 4865087 | ELSTER | Kvarh(Lead/Lag) | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ENERGY INPUT AT 66/33/11KV LEVEL | [8 empty] | 7.288 |  |  |  |  | 1.03
| (B) NET ENERGY TO EAST | [8 empty] | 7.288 |  |  |  |  | 1.03
DECEMBER-2013
BYPL(-) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
KASHMIRI GATE
1 | CIVIL LINE | 4864902 | ELSTER | Kvarh(Lead/Lag) | -400 | 448 | 32 | 416 | -166400 | -0.1664 | 0 | 0 | 0 | 0 | 0
2 | CIVIL LINE-2 | 5128405 | ELSTER | Kvarh(Lead/Lag) | -500 | 1838 | 1571 | 267 | -133500 | -0.1335 | 2047 | 2036 | 11 | -5500 | -0.0055
EXPORT TO NDMC FROM PARK STREET
3 | BAIRD RD.1 | 4865136 | ELSTER | Kvarh(Lead/Lag) | -200 | 42728 | 41653 | 1075 | -215000 | -0.215 | 72223 | 72223 | 0 | 0 | 0
4 | BAIRD RD.2 | 4865137 | ELSTER | Kvarh(Lead/Lag) | -100 | 70493 | 70493 | 0 | 0 | 0 | 139686 | 139686 | 0 | 0 | 0
5 | NIRMAN BHAWAN | 4865138 | ELSTER | Kvarh(Lead/Lag) | -200 | 983165 | 983645 | -480 | 96000 | 0.096 | 1904 | 1904 | 0 | 0 | 0
6 | H.LANE | 4865139 | ELSTER | Kvarh(Lead/Lag) | -200 | 69713 | 68759 | 954 | -190800 | -0.1908 | 88791 | 88791 | 0 | 0 | 0
7 | 66 KV BD MARG-I | 4865050 | ELSTER | Kvarh(Lead/Lag) | -800 | 4982 | 4038 | 944 | -755200 | -0.7552 | 1140 | 1140 | 0 | 0 | 0
8 | 66 KV BD MARG-II | 4864949 | ELSTER | Kvarh(Lead/Lag) | -2000 | 13532 | 13421 | 111 | -222000 | -0.222 | 924 | 924 | 0 | 0 | 0
9 | 66KV DMRC-I | 5128434 | ELSTER | Kvarh(Lead/Lag) | -800 | 984467 | 985046 | -579 | 463200 | 0.4632 | 993049 | 993049 | 0 | 0 | 0
10 | 66KV DMRC-II | 5128430 | ELSTER | Kvarh(Lead/Lag) | -800 | 991894 | 993695 | -1801 | 1440800 | 1.4408 | 994960 | 994960 | 0 | 0 | 0
11 | 66KV GUEST HOUSE | 5128445 | ELSTER | Kvarh(Lead/Lag) | -800 | 996344 | 997768 | -1424 | 1139200 | 1.1392 | 997872 | 997877 | -5 | 4000 | 0.004
EXPORT TO SOUTH & WEST FROM PARK STREET
12 | 66KV R VALLEY-1 | 4864951 | ELSTER | Kvarh(Lead/Lag) | -1000 | 994343 | 995061 | -718 | 718000 | 0.718 | 37395 | 37395 | 0 | 0 | 0
13 | 66KV R VALLEY-2 | 4902501 | ELSTER | Kvarh(Lead/Lag) | -1333.33 | 994435 | 994977 | -542 | 722664.86 | 0.72266 | 999561 | 999561 | 0 | 0 | 0
EXPORT TO NORTH from SHASTRI PARK
14 | PUSA GRID-I | 4864843 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1564 | 1539 | 25 | -25000 | -0.025 | 21101 | 21080 | 21 | -21000 | -0.021
15 | PUSA GRID-II | 4864844 | ELSTER | Kvarh(Lead/Lag) | -1000 | 269 | 303 | -34 | 34000 | 0.034 | 2013 | 2027 | -14 | 14000 | 0.014
DMS
16 | 33KV PANDAV NGR | 4865169 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1194 | 1230 | -36 | 36000 | 0.036 | 60903 | 60903 | 0 | 0 | 0
EXCHANGE OF ENERGY 11KV
EXPORTS
B.G.ROAD
17 | CSA | 4865091 | ELSTER | Kvarh(Lead/Lag) | -500 | 5452 | 5393 | 59 | -29500 | -0.0295 | 28792 | 28716 | 76 | -38000 | -0.038
18 | DCM NO.1 | 4902530 | ELSTER | Kvarh(Lead/Lag) | -500 | 3601 | 3556 | 45 | -22500 | -0.0225 | 26659 | 26616 | 43 | -21500 | -0.0215
19 | DCM NO.2 | 4902531 | ELSTER | Kvarh(Lead/Lag) | -500 | 5206 | 5121 | 85 | -42500 | -0.0425 | 14551 | 14543 | 8 | -4000 | -0.004
20 | SADAR S/S | 4865072 | ELSTER | Kvarh(Lead/Lag) | -666.6667 | 566 | 514 | 52 | -34666.6667 | -0.034667 | 554 | 546 | 8 | -5333.3333 | -0.0053333
KASHMIRI GATE
21 | 20MVA TX. | 4864807 | ELSTER | Kvarh(Lead/Lag) | -100 | 138816 | 135809 | 3007 | -300700 | -0.3007 | 23963 | 23936 | 27 | -2700 | -0.0027
22 | FLY OVER | 4865086 | ELSTER | Kvarh(Lead/Lag) | -100 | 21001 | 20688 | 313 | -31300 | -0.0313 | 41325 | 41312 | 13 | -1300 | -0.0013
D.M.S.
23 | PHILIPS | 4902535 | ELSTER | Kvarh(Lead/Lag) | -100 | 993917 | 994664 | -747 | 74700 | 0.0747 | 5898 | 5898 | 0 | 0 | 0
24 | 69 NG ROAD | 4902536 | ELSTER | Kvarh(Lead/Lag) | -100 | 7991 | 8046 | -55 | 5500 | 0.0055 | 15336 | 15336 | 0 | 0 | 0
25 | J BLOCK KIRTI NGR | 4902537 | ELSTER | Kvarh(Lead/Lag) | -100 | 22445 | 21664 | 781 | -78100 | -0.0781 | 54105 | 54092 | 13 | -1300 | -0.0013
26 | H BLOCK | 4902579 | ELSTER | Kvarh(Lead/Lag) | -100 | 4695 | 4748 | -53 | 5300 | 0.0053 | 999974 | 999975 | -1 | 100 | 0.0001
27 | SHADI KHAM PUR | 4902539 | ELSTER | Kvarh(Lead/Lag) | -100 | 998783 | 998810 | -27 | 2700 | 0.0027 | 131 | 131 | 0 | 0 | 0
28 | BREAK FAST | 4902540 | ELSTER | Kvarh(Lead/Lag) | -100 | 15 | 15 | 0 | 0 | 0 | 13398 | 13398 | 0 | 0 | 0
FAIZ ROAD
29 | TIBIA COLLEGE-1 | 4902541 | ELSTER | Kvarh(Lead/Lag) | -100 | 17398 | 16890 | 508 | -50800 | -0.0508 | 71878 | 71877 | 1 | -100 | -0.0001
30 | TIBIA COLLEGE-2 | 4902542 | ELSTER | Kvarh(Lead/Lag) | -100 | 12965 | 12610 | 355 | -35500 | -0.0355 | 62674 | 62590 | 84 | -8400 | -0.0084
31 | MANAK PURA | 4902543 | ELSTER | Kvarh(Lead/Lag) | -100 |  |  |  |  | 0.083133 |  |  |  |  | 0 | Assessment (Meter faulty)
[10 empty] | 2.4877 |  |  |  |  | -0.091033
DECEMBER-2013
EXECUTIVE SUMMARY
ENERGY RELEASED TO CENTRAL
| 1) ENERGY AT 66/33/11 KV LEVEL (Refre A- Page -1) | [8 empty] | -3.8203 |  |  |  |  | -8.2049
| 2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer C Page-3) | [8 empty] | 2.4877 |  |  |  |  | -0.091033
| 3) FROM ROHTAK ROAD (REFER ENERGY BALANCE SHEET ROHTAK ROAD ENCL.) | [8 empty] | -0.9538 |  |  |  |  | 0.0182
| TOTAL ENERGY TO BSES YAMUNA POWER LTD. - CENTRAL PART | [8 empty] | -2.2864 |  |  |  |  | -8.2777
ENERGY RELEASED TO EAST
| 1) ENERGY AT 66/33/11 KV LEVEL (Refre B- Page -2) | [8 empty] | 7.288 |  |  |  |  | 1.03
| NET ENERGY TO BSES YAMUNA POWER LIMITED | [8 empty] | 5.0016 |  |  |  |  | -7.2477
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | 5.0016 | (REACTIVE MUs) |  |  |  | -7.2477 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | 0.21176 | (REACTIVE MUs) |  |  |  | -1.8331 | (REACTIVE MUs)
[9 empty] | TOTAL | 5.2134 | (REACTIVE MUs) |  |  |  | -9.0809 | (REACTIVE MUs)

## BRPL
DELHI TRANSCO LIMITED | [14 empty] | DECEMBER-2013
REACTIVE ENERGY CONSUMPTION STATEMENT
CUSTOMER-BSES RAJDHANI POWER LIMITED
BRPL (+) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
I.P.STATION
1 | BAY-24 | 4865180 | ELSTER | Kvarh(Lead/Lag) | 4000 | 998057 | 998056 | 1 | 4000 | 0.004 | 8806 | 8806 | 0 | 0 | 0
2 | BAY-25 | 4865095 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 987298 | 987893 | -595 | -793331.35 | -0.79333 | 673971 | 674011 | -40 | -53333.2 | -0.053333
3 | BAY-13 | 4865166 | ELSTER | Kvarh(Lead/Lag) | 1000 |  |  |  |  | 0.052 |  |  |  |  | 0.078 | Metering not in order
4 | BAY-53 | 4865151 | ELSTER | Kvarh(Lead/Lag) | 1000 | 11880 | 11782 | 98 | 98000 | 0.098 | 999564 | 999554 | 10 | 10000 | 0.01
5 | BAY-54 | 4865152 | ELSTER | Kvarh(Lead/Lag) | 300 | 1605 | 1605 | 0 | 0 | 0 | 112 | 112 | 0 | 0 | 0
6 | BAY-7 | 4865096 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  |  |  | 0.0179 |  |  |  |  | 0.1758 | Metering not in order
7 | BAY-37 | 4865097 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  |  |  | -0.6152 |  |  |  |  | 0 | Assessment (reading Error )
8 | BAY-9 | 4864789 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  |  |  | -0.0087 |  |  |  |  | -0.0269 | Metering not in order
9 | BAY-5 LAJPAT NAGAR | 4865181 | ELSTER | Kvarh(Lead/Lag) | 900 |  |  |  |  | -0.0054 |  |  |  |  | -0.1071 | Metering not in order
PAAPANKALAN
10 | Tx.1 | 4864973 | ELSTER | Kvarh(Lead/Lag) | -1000 | 989747 | 989621 | 126 | -126000 | -0.126 | 946102 | 946125 | -23 | 23000 | 0.023
11 | Tx.2 | 4864974 | ELSTER | Kvarh(Lead/Lag) | -1000 | 987162 | 987097 | 65 | -65000 | -0.065 | 951148 | 951156 | -8 | 8000 | 0.008
12 | Tx.3 | 4864975 | ELSTER | Kvarh(Lead/Lag) | -1000 | 979146 | 980302 | -1156 | 1156000 | 1.156 | 930396 | 930415 | -19 | 19000 | 0.019
13 | Tx.4 | 4864976 | ELSTER | Kvarh(Lead/Lag) | -1000 | 994111 | 995258 | -1147 | 1147000 | 1.147 | 950681 | 950698 | -17 | 17000 | 0.017
PAAPANKALAN-II
14 | Tx.1 | 5128437 | ELSTER | Kvarh(Lead/Lag) | -1000 | 993307 | 994614 | -1307 | 1307000 | 1.307 | 980412 | 980412 | 0 | 0 | 0
15 | Tx.2 | 5128439 | ELSTER | Kvarh(Lead/Lag) | -1000 | 19402 | 16737 | 2665 | -2665000 | -2.665 | 985418 | 985418 | 0 | 0 | 0
16 | Tx.3 | 5128460 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1006212 | 999495 | 6717 | -6717000 | -6.717 | 2 | 2 | 0 | 0 | 0
NAJAFGARH
17 | Tx.1 | 4864977 | ELSTER | Kvarh(Lead/Lag) | -1000 | 2342 | 2463 | -121 | 121000 | 0.121 | 999528 | 999529 | -1 | 1000 | 0.001
18 | Tx.2 | 4864970 | ELSTER | Kvarh(Lead/Lag) | -1000 | 9559 | 10901 | -1342 | 1342000 | 1.342 | 1780 | 1951 | -171 | 171000 | 0.171
19 | Tx.3 | 4864971 | ELSTER | Kvarh(Lead/Lag) | -1000 | 25598 | 26145 | -547 | 547000 | 0.547 | 6299 | 6300 | -1 | 1000 | 0.001
20 | Tx.4 | 4864995 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999951 | 1000006 | -55 | 55000 | 0.055 | 999949 | 999997 | -48 | 48000 | 0.048
IMPORT
MANGOLPURI
21 | NANGLOI-2 (03) IMP. | 4864955 | ELSTER | Kvarh(Lead/Lag) | 1000 | 9095 | 8717 | 378 | 378000 | 0.378 | 7061 | 7047 | 14 | 14000 | 0.014
LODHI ROAD
22 | Tx.1 | 4864908 | ELSTER | Kvarh(Lead/Lag) | -1000 | 911784 | 912441 | -657 | 657000 | 0.657 | 890303 | 890303 | 0 | 0 | 0
23 | Tx.2 | 4864909 | ELSTER | Kvarh(Lead/Lag) | -1000 | 958336 | 959840 | -1504 | 1504000 | 1.504 | 857225 | 857225 | 0 | 0 | 0
OKHLA
24 | Tx.1 (66 KV) | 4864964 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999979 | 999434 | 545 | -545000 | -0.545 | 972497 | 972761 | -264 | 264000 | 0.264
25 | Tx.2 (66 KV) | 4864965 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999019 | 999784 | -765 | 765000 | 0.765 | 956312 | 957002 | -690 | 690000 | 0.69
26 | Tx.1 (33 KV) | 4864890 | ELSTER | Kvarh(Lead/Lag) | -1000 | 996147 | 996056 | 91 | -91000 | -0.091 | 956880 | 956880 | 0 | 0 | 0
27 | Tx.2 (33 KV) | 4864891 | ELSTER | Kvarh(Lead/Lag) | -1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | Tx.3 (33 KV) | 4864906 | ELSTER | Kvarh(Lead/Lag) | -1000 | 998827 | 998633 | 194 | -194000 | -0.194 | 889905 | 889929 | -24 | 24000 | 0.024
29 | Tx.4 (33 KV) | 4864907 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997789 | 997680 | 109 | -109000 | -0.109 | 869236 | 869275 | -39 | 39000 | 0.039
BRPL(+) continue | [14 empty] | DECEMBER-2013
VASANT KUNJ
30 | Tx.1 | 4864988 | ELSTER | Kvarh(Lead/Lag) | -1000 | 996667 | 996623 | 44 | -44000 | -0.044 | 972687 | 972766 | -79 | 79000 | 0.079
31 | Tx.2 | 4864989 | ELSTER | Kvarh(Lead/Lag) | -1000 | 998310 | 998309 | 1 | -1000 | -0.001 | 988842 | 988999 | -157 | 157000 | 0.157
32 | Tx.3 | 4864979 | ELSTER | Kvarh(Lead/Lag) | -2000 | 995616 | 994826 | 790 | -1580000 | -1.58 | 970107 | 970107 | 0 | 0 | 0
MEHRAULI
33 | Tx.1 | 4864966 | ELSTER | Kvarh(Lead/Lag) | -1000 | 996358 | 996559 | -201 | 201000 | 0.201 | 915270 | 915355 | -85 | 85000 | 0.085
34 | Tx.2 | 4864967 | ELSTER | Kvarh(Lead/Lag) | -1000 | 995227 | 995227 | 0 | 0 | 0 | 928164 | 928164 | 0 | 0 | 0
35 | Tx.3 | 4865019 | ELSTER | Kvarh(Lead/Lag) | -1000 | 996300 | 996497 | -197 | 197000 | 0.197 | 919341 | 919411 | -70 | 70000 | 0.07 | Check Meter Data used
36 | Tx.4 | 5128468 | ELSTER | Kvarh(Lead/Lag) | -1000 | 996486 | 999311 | -2825 | 2825000 | 2.825 | 999934 | 999999 | -65 | 65000 | 0.065
RIDGE VALLEY
37 | Tx-1 | 4864827 | ELSTER | Kvarh(Lead/Lag) | -666.666 | 988485 | 991231 | -2746 | 1830664.836 | 1.8307 | 984337 | 984337 | 0 | 0 | 0
38 | Tx-2 | 4864828 | ELSTER | Kvarh(Lead/Lag) | -666.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DIAL
39 | Tx-1 | 4865024 | ELSTER | Kvarh(Lead/Lag) | -2000 | 1600 | 1449 | 151 | -302000 | -0.302 | 1494 | 1475 | 19 | -38000 | -0.038
40 | Tx-2 | 4864920 | ELSTER | Kvarh(Lead/Lag) | -2000 | 998533 | 998367 | 166 | -332000 | -0.332 | 642 | 627 | 15 | -30000 | -0.03
MASJID MOD
41 | Tx-1 | 5128414 | ELSTER | Kvarh(Lead/Lag) | -1000 | 946519 | 948577 | -2058 | 2058000 | 2.058 | 995781 | 995781 | 0 | 0 | 0
42 | Tx-2 | 5128416 | ELSTER | Kvarh(Lead/Lag) | -1000 | 957885 | 959683 | -1798 | 1798000 | 1.798 | 996014 | 996014 | 0 | 0 | 0
MUNDKA
43 | 66KV NANGLOI | 5100228 | ELSTER | Kvarh(Lead/Lag) | 800 | 994101 | 994101 | 0 | 0 | 0 | 1447 | 1447 | 0 | 0 | 0
44 | 66KV NGL. WATER WORKS | 5128441 | ELSTER | Kvarh(Lead/Lag) | 800 | 19785 | 19357 | 428 | 342400 | 0.3424 | 1045 | 1045 | 0 | 0 | 0
45 | 66KV DMRC | 5128443 | ELSTER | Kvarh(Lead/Lag) | 800 | 951178 | 954748 | -3570 | -2856000 | -2.856 | 999692 | 999692 | 0 | 0 | 0
46 | 66KV NGL. T-OFF MGL P | 5128407 | ELSTER | Kvarh(Lead/Lag) | -2000 | 999423 | 999423 | 0 | 0 | 0 | 999980 | 999980 | 0 | 0 | 0
PARK STREET
47 | 66KV R VALLEY-1 | 4864951 | ELSTER | Kvarh(Lead/Lag) | 1000 | 994343 | 995061 | -718 | -718000 | -0.718 | 37395 | 37395 | 0 | 0 | 0
48 | 66KV R VALLEY-2 | 4902501 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 994435 | 994977 | -542 | -722664.86 | -0.72266 | 999561 | 999561 | 0 | 0 | 0
SARITA VIHAR
49 | TX-1 | 4864990 | ELSTER | Kvarh(Lead/Lag) | -1000 | 10596 | 9604 | 992 | -992000 | -0.992 | 975123 | 975131 | -8 | 8000 | 0.008
50 | Tx-2 | 4864991 | ELSTER | Kvarh(Lead/Lag) | -1000 | 2730 | 816 | 1914 | -1914000 | -1.914 | 989738 | 989740 | -2 | 2000 | 0.002
NARAINA
51 | GOPI NATH BAZAAR | 4865092 | ELSTER | Kvarh(Lead/Lag) | 100 | 14265 | 13861 | 404 | 40400 | 0.0404 | 14243 | 14070 | 173 | 17300 | 0.0173
SUDARSHAN PARK
52 | VISHAL | 4864898 | ELSTER | Kvarh(Lead/Lag) | 100 | 11533 | 11735 | -202 | -20200 | -0.0202 | 61483 | 61487 | -4 | -400 | -0.0004
REWARI LINE
53 | 33KV B/C | 4865174 | ELSTER | Kvarh(Lead/Lag) | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KANJAWALA
54 | 66KV DMRC | 4864961 | ELSTER | Kvarh(Lead/Lag) | 1000 | 949018 | 950752 | -1734 | -1734000 | -1.734 | 992454 | 992454 | 0 | 0 | 0
A.I.I.M.S.
55 | 11KV VIKAS SADAN | 4902586 | ELSTER | Kvarh(Lead/Lag) | 100 | 1380 | 1303 | 77 | 7700 | 0.0077 | 9911 | 9880 | 31 | 3100 | 0.0031
56 | 11KV NDSE | 4902587 | ELSTER | Kvarh(Lead/Lag) | 100 | 9385 | 9084 | 301 | 30100 | 0.0301 | 21795 | 21700 | 95 | 9500 | 0.0095
SUM OF ENERGY RELEASED AT 66/33/11 KV LEVEL | [9 empty] | -4.6693 |  |  |  |  | 1.823
BRPL (-) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 % |  |  | DECEMBER-2013
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
TILAK MARG
1 | EXHB-II | 4865143 | ELSTER | Kvarh(Lead/Lag) | -100 | 36375 | 36375 | 0 | 0 | 0 | 892330 | 891566 | 764 | -76400 | -0.0764
EXPORT TO EAST & CENTRE
RIDGE VALLEY
2 | O/G SHANKAR RD.1 | 4865134 | ELSTER | Kvarh(Lead/Lag) | -100 | 111280 | 110284 | 996 | -99600 | -0.0996 | 1617 | 1617 | 0 | 0 | 0
3 | O/G SHANKAR RD.2 | 4865135 | ELSTER | Kvarh(Lead/Lag) | -100 | 105385 | 103629 | 1756 | -175600 | -0.1756 | 2383 | 2383 | 0 | 0 | 0
4 | KHYBER LANE-1 EXP. | 4864804 | ELSTER | Kvarh(Lead/Lag) | -100 | 997066 | 997370 | -304 | 30400 | 0.0304 | 999978 | 999978 | 0 | 0 | 0
5 | KHYBER LANE-2 EXP. | 4865163 | ELSTER | Kvarh(Lead/Lag) | -100 | 996724 | 996770 | -46 | 4600 | 0.0046 | 999920 | 999920 | 0 | 0 | 0
EXPORTS(*)
EXPORT TO NDMC
6 | SPM NO.1/ BAPUDHAM | 4864845 | ELSTER | Kvarh(Lead/Lag) | -2000 | 1057 | 1054 | 3 | -6000 | -0.006 | 73243 | 73243 | 0 | 0 | 0
7 | SPM NO.2 | 4864862 | ELSTER | Kvarh(Lead/Lag) | -1000 | 7453 | 6563 | 890 | -890000 | -0.89 | 81 | 81 | 0 | 0 | 0
8 | NEHRU PARK | 4865142 | ELSTER | Kvarh(Lead/Lag) | -500 | 895535 | 893843 | 1692 | -846000 | -0.846 | 54462 | 54462 | 0 | 0 | 0
EXPORT TO NDMC
9 | SHAN NAGAR 1 | 4865093 | ELSTER | Kvarh(Lead/Lag) | -100 | 59979 | 58401 | 1578 | -157800 | -0.1578 | 58837 | 58837 | 0 | 0 | 0
10 | SHAN NAGAR 2 | 4865094 | ELSTER | Kvarh(Lead/Lag) | -100 | 53124 | 51134 | 1990 | -199000 | -0.199 | 56893 | 56893 | 0 | 0 | 0
11 | VIDYUT BHAWAN | 4865144 | ELSTER | Kvarh(Lead/Lag) | -200 | 85677 | 85214 | 463 | -92600 | -0.0926 | 112978 | 112978 | 0 | 0 | 0
EXPORTS(*)
A.I.I.M.S.
12 | KILOKARI | 4864892 | ELSTER | Kvarh(Lead/Lag) | 500 | 1749 | 2206 | -457 | -228500 | -0.2285 | 17884 | 17889 | -5 | -2500 | -0.0025
13 | SIRI FORT | 4864826 | ELSTER | Kvarh(Lead/Lag) | 83.3333 | 3500 | 3889 | -389 | -32416.6667 | -0.032417 | 979525 | 979525 | 0 | 0 | 0
14 | RIDGE VALLEY | 4864791 | ELSTER | Kvarh(Lead/Lag) | 166.6667 | 989720 | 990679 | -959 | -159833.3333 | -0.15983 | 993688 | 993688 | 0 | 0 | 0
KIDWAI NAGAR
15 | TR(10MVA)KILOKRI#2 | 4865133 | ELSTER | Kvarh(Lead/Lag) | -100 | 294510 | 292449 | 2061 | -206100 | -0.2061 | 44379 | 44320 | 59 | -5900 | -0.0059
EXHIBITION I
16 | TILAK MARG | 4865076 | ELSTER | Kvarh(Lead/Lag) | -100 | 3725 | 3491 | 234 | -23400 | -0.0234 | 18309 | 18159 | 150 | -15000 | -0.015
17 | KRISHI BHAWAN | 4865077 | ELSTER | Kvarh(Lead/Lag) | -100 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
REWARI LINE (ENERGY EXCHANGE WITH NDPL)
18 | 20 MVA TX.-2(Delv.) | 4864824 | ELSTER | Kvarh(Lead/Lag) | -100 | 804 | 804 | 0 | 0 | 0 | 77729 | 77721 | 8 | -800 | -0.0008
EXCHANGE OF ENERGY 11KV
EXPORTS
VISHAL
19 | RAMESH NAGAR-1 | 4865090 | ELSTER | Kvarh(Lead/Lag) | -100 | 9213 | 9217 | -4 | 400 | 0.0004 | 28708 | 28824 | -116 | 11600 | 0.0116
20 | BALI NAGAR -1 | 4902519 | ELSTER | Kvarh(Lead/Lag) | -100 | 10525 | 10530 | -5 | 500 | 0.0005 | 51109 | 51144 | -35 | 3500 | 0.0035
21 | ESI HOSPITAL | 4902520 | ELSTER | Kvarh(Lead/Lag) | -100 | 15813 | 15718 | 95 | -9500 | -0.0095 | 53799 | 53261 | 538 | -53800 | -0.0538
S.B.MILL
22 | MOTI NAGAR KIOSK | 4902521 | ELSTER | Kvarh(Lead/Lag) | -100 | 42428 | 42213 | 215 | -21500 | -0.0215 | 17222 | 16639 | 583 | -58300 | -0.0583
23 | 53 RAMA ROAD | 4902522 | ELSTER | Kvarh(Lead/Lag) | -100 | 840 | 840 | 0 | 0 | 0 | 185 | 185 | 0 | 0 | 0
24 | BREAK FAST | 4902523 | ELSTER | Kvarh(Lead/Lag) | -100 | 999815 | 999815 | 0 | 0 | 0 | 999943 | 999943 | 0 | 0 | 0
25 | 70 RAMA ROAD | 4902524 | ELSTER | Kvarh(Lead/Lag) | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | MOTI NAGAR 2 | 4902605 | ELSTER | Kvarh(Lead/Lag) | -1333.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | NAJAFGARH ROAD | 4902526 | ELSTER | Kvarh(Lead/Lag) | -100 | 16873 | 16862 | 11 | -1100 | -0.0011 | 15236 | 14755 | 481 | -48100 | -0.0481
28 | PHILIPS | 4902529 | ELSTER | Kvarh(Lead/Lag) | -44.44 | 999086 | 999372 | -286 | 12709.84 | 0.01271 | 587 | 761 | -174 | 7732.56 | 0.0077326
29 | ZAKHIRA | 4865087 | ELSTER | Kvarh(Lead/Lag) | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REWARI LINE (11KV TRANSFER OF ENERGY)
30 | BSES -NDPL(EX.) ON BUS-1&2 | 4902577 | ELSTER | Kvarh(Lead/Lag) | 400 | 995589 | 995589 | 0 | 0 | 0 | 36 | 36 | 0 | 0 | 0
31 | BSES -NDPL(EX.) ON BUS-2&3 | 4902516 | ELSTER | Kvarh(Lead/Lag) | -100 | 999273 | 999273 | 0 | 0 | 0 | 999398 | 999398 | 0 | 0 | 0
TOTAL OF ENERGY AT INTER COMPANY EXCHANGE POINTS | [9 empty] | -3.1003 |  |  |  |  | -0.23797
DECEMBER-2013
EXECUTIVE SUMMERY BSES R.P. LTD.
1) ENERGY RELEASED AT 66/33/11 KV LEVEL (REFER SHEET BRPL (+)) | [9 empty] | -4.6693 |  |  |  |  | 1.823
2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer sheet BRPL(-)) | [9 empty] | -3.1003 |  |  |  |  | -0.23797
3)ENERGY RECEIVED FROM ROHTAK ROAD (REFER ROHTAK ROAD SHEET ENC.) | [9 empty] | 0.84323 |  |  |  |  | 0.38219
4) ENERGY RELEASED TO MES BY BRPL | [9 empty] | -0.2151 |  |  |  |  | -0.0381
NET ENERGY TO BSES RAJDHANI POWER LIMITED | [9 empty] | -7.1415 |  |  |  |  | 1.9291
Meter changed on 28/11/13
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | -7.1415 | (REACTIVE MUs) |  |  |  | 1.9291 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | 0.36649 | (REACTIVE MUs) |  |  |  | -3.1726 | (REACTIVE MUs)
[9 empty] | TOTAL | -6.7751 | (REACTIVE MUs) |  |  |  | -1.2435 | (REACTIVE MUs)

## NDMC
DELHI TRANSCO LIMITED | [15 empty] | DECEMBER-2013
REACTIVE ENERGY CONSUMPTION STATEMENT
CUSTOMER-NDMC
NDMC(+) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
AT PARK STREET
EXPORT TO NDMC
1 | BAIRD RD.1 | 4865136 | ELSTER | Kvarh(Lead/Lag) | 200 | 42728 | 41653 | 1075 | 215000 | 0.215 | 72223 | 72223 | 0 | 0 | 0
2 | BAIRD RD.2 | 4865137 | ELSTER | Kvarh(Lead/Lag) | 100 | 70493 | 70493 | 0 | 0 | 0 | 139686 | 139686 | 0 | 0 | 0
3 | NIRMAN BHAWAN | 4865138 | ELSTER | Kvarh(Lead/Lag) | 200 | 983165 | 983645 | -480 | -96000 | -0.096 | 1904 | 1904 | 0 | 0 | 0
4 | H.LANE | 4865139 | ELSTER | Kvarh(Lead/Lag) | 200 | 69713 | 68759 | 954 | 190800 | 0.1908 | 88791 | 88791 | 0 | 0 | 0
5 | 66 KV BD MARG-I | 4865050 | ELSTER | Kvarh(Lead/Lag) | 800 | 4982 | 4038 | 944 | 755200 | 0.7552 | 1140 | 1140 | 0 | 0 | 0
6 | 66 KV BD MARG-II | 4864949 | ELSTER | Kvarh(Lead/Lag) | 2000 | 13532 | 13421 | 111 | 222000 | 0.222 | 924 | 924 | 0 | 0 | 0
7 | 66KV DMRC-I | 5128434 | ELSTER | Kvarh(Lead/Lag) | 800 | 984467 | 985046 | -579 | -463200 | -0.4632 | 993049 | 993049 | 0 | 0 | 0
8 | 66KV DMRC-II | 5128430 | ELSTER | Kvarh(Lead/Lag) | 800 | 991894 | 993695 | -1801 | -1440800 | -1.4408 | 994960 | 994960 | 0 | 0 | 0
9 | 66KV GUEST HOUSE | 5128445 | ELSTER | Kvarh(Lead/Lag) | 800 | 996344 | 997768 | -1424 | -1139200 | -1.1392 | 997872 | 997877 | -5 | -4000 | -0.004
I.P.STATION EXPORT TO NDMC
10 | BAY-2 (N BWN) | 4865124 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  |  |  | 0.0027 |  |  |  |  | 0.4049 | Metering not in order
11 | BAY-4 (E LANE) | 4865125 | ELSTER | Kvarh(Lead/Lag) | 100 | 6605 | 6605 | 0 | 0 | 0 | 470995 | 470995 | 0 | 0 | 0
12 | BAY-6 (T MARG) | 4865126 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  |  |  | 0 |  |  |  |  | 0.7396 | Metering not in order
13 | BAY-10 (E LANE) | 4865127 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  |  |  | -0.0078 |  |  |  |  | 0.1386 | Metering not in order
14 | BAY-16 (N BWN) | 4865128 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  |  |  | 0 |  |  |  |  | 0.3322 | Metering not in order
15 | BAY-28 (C PLACE) | 4865129 | ELSTER | Kvarh(Lead/Lag) | 100 | 999881 | 999881 | 0 | 0 | 0 | 175798 | 175798 | 0 | 0 | 0
16 | BAY-38 (C PLACE) | 4865130 | ELSTER | Kvarh(Lead/Lag) | 100 | 13432 | 13432 | 0 | 0 | 0 | 259759 | 259759 | 0 | 0 | 0
17 | BAY-42 (C PLACE) | 4865132 | ELSTER | Kvarh(Lead/Lag) | 100 | 51073 | 51073 | 0 | 0 | 0 | 704427 | 704427 | 0 | 0 | 0
G.T.
18 | VIDYUT BHAWAN-1 | 4865037 | ELSTER | Kvarh(Lead/Lag) | 1100 | 0 | 0 | 0 | 0 | 0 | 73735 | 73436 | 299 | 328900 | 0.3289
19 | VIDYUT BHAWAN-2 | 4865038 | ELSTER | Kvarh(Lead/Lag) | 1000 | 3148 | 3269 | -121 | -121000 | -0.121 | 37831 | 37884 | -53 | -53000 | -0.053
20 | SCHOOL LANE-1 | 4865039 | ELSTER | Kvarh(Lead/Lag) | 1100 | 0 | 0 | 0 | 0 | 0 | 143906 | 143008 | 898 | 987800 | 0.9878
21 | SCHOOL LANE-2 | 4865040 | ELSTER | Kvarh(Lead/Lag) | 1000 | 8529 | 8771 | -242 | -242000 | -0.242 | 53179 | 53221 | -42 | -42000 | -0.042
[10 empty] | -0.363 |  |  |  |  | 1.2217
RIDGE VALLEY
22 | SPM NO.1/ BAPUDHAM | 4864845 | ELSTER | Kvarh(Lead/Lag) | 2000 | 1057 | 1054 | 3 | 6000 | 0.006 | 73243 | 73243 | 0 | 0 | 0
23 | SPM NO.2 | 4864862 | ELSTER | Kvarh(Lead/Lag) | 1000 | 7453 | 6563 | 890 | 890000 | 0.89 | 81 | 81 | 0 | 0 | 0
24 | NEHRU PARK | 4865142 | ELSTER | Kvarh(Lead/Lag) | 500 | 895535 | 893843 | 1692 | 846000 | 0.846 | 54462 | 54462 | 0 | 0 | 0
A.I.I.M.S.
25 | KILOKARI | 4864892 | ELSTER | Kvarh(Lead/Lag) | -500 | 1749 | 2206 | -457 | 228500 | 0.2285 | 17884 | 17889 | -5 | 2500 | 0.0025
26 | SIRI FORT | 4864826 | ELSTER | Kvarh(Lead/Lag) | -83.3333 | 3500 | 3889 | -389 | 32416.6667 | 0.032417 | 979525 | 979525 | 0 | 0 | 0
27 | RIDGE VALLEY | 4864791 | ELSTER | Kvarh(Lead/Lag) | -166.6667 | 989720 | 990679 | -959 | 159833.3333 | 0.15983 | 993688 | 993688 | 0 | 0 | 0
DECEMBER-2013
NDMC(+) Continue…
TRAUMA CENTRE
26 | 33KV TX-1 | 5128418 | ELSTER | Kvarh(Lead/Lag) | -1000 | 984251 | 984543 | -292 | 292000 | 0.292 | 991560 | 991888 | -328 | 328000 | 0.328
ELECTRIC LANE
27 | 33KV TX-1 | 5128422 | ELSTER | Kvarh(Lead/Lag) | -1000 | 988824 | 989987 | -1163 | 1163000 | 1.163 | 990826 | 990826 | 0 | 0 | 0
28 | 33KV TX-2 | 5128428 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999362 | 1000000 | -638 | 638000 | 0.638 | 29 | 0 | 29 | -29000 | -0.029
KIDWAI NAGAR
29 | TR(10MVA) KILOKRI#2 | 4865133 | ELSTER | Kvarh(Lead/Lag) | 100 | 294510 | 292449 | 2061 | 206100 | 0.2061 | 44379 | 44320 | 59 | 5900 | 0.0059
EXHIBITION I
30 | TILAK MARG | 4865076 | ELSTER | Kvarh(Lead/Lag) | 100 | 3725 | 3491 | 234 | 23400 | 0.0234 | 18309 | 18159 | 150 | 15000 | 0.015
31 | KRISHI BHAWAN | 4865077 | ELSTER | Kvarh(Lead/Lag) | 100 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
LODHI ROAD
32 | SHAN NAGAR 1 | 4865093 | ELSTER | Kvarh(Lead/Lag) | 100 | 59979 | 58401 | 1578 | 157800 | 0.1578 | 58837 | 58837 | 0 | 0 | 0
33 | SHAN NAGAR 2 | 4865094 | ELSTER | Kvarh(Lead/Lag) | 100 | 53124 | 51134 | 1990 | 199000 | 0.199 | 56893 | 56893 | 0 | 0 | 0
34 | VIDYUT BHAWAN (exp) | 4865144 | ELSTER | Kvarh(Lead/Lag) | 200 | 85677 | 85214 | 463 | 92600 | 0.0926 | 112978 | 112978 | 0 | 0 | 0
TILAK MARG
35 | EXHB-II | 4865143 | ELSTER | Kvarh(Lag) | 100 | 36375 | 36375 | 0 | 0 | 0 | 892330 | 891566 | 764 | 76400 | 0.0764
NDMC(-) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
AIIMS
1 | 11KV VIKAS SADAN | 4902586 | ELSTER | Kvarh(Lead/Lag) | -100 | 1380 | 1303 | 77 | -7700 | -0.0077 | 9911 | 9880 | 31 | -3100 | -0.0031
2 | 11KV NDSE | 4902587 | ELSTER | Kvarh(Lead/Lag) | -100 | 9385 | 9084 | 301 | -30100 | -0.0301 | 21795 | 21700 | 95 | -9500 | -0.0095
TOTAL ENERGY RELEASED AT 66/33/11 KV LEVEL | [9 empty] | 2.7726 |  |  |  |  | 3.2192
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
| ENERGY TO NDMC | [8 empty] | 2.7726 |  |  |  |  | 3.2192
| SHARED DISTRIBUTION GENERATED BY GENCO | [8 empty] | 0.044834 |  |  |  |  | -0.38811
| TOTAL ENERGY TO NDMC | [8 empty] | 2.8174 |  |  |  |  | 2.8311

## MES
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | DECEMBER-2013
CUSTOMER- MES
[8 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
MES(+)
FED FROM DTL SYSTEM.
NARAINA ( ON 33KV)
1 | KHBR LANE-1-EXP. | 4864848 | ELSTER | Kvarh(Lead/Lag) | 1000 | 1024 | 928 | 96 | 96000 | 0.096 | 23208 | 23078 | 130 | 130000 | 0.13
2 | KHBR LANE-2 -EXP. | 4864849 | ELSTER | Kvarh(Lead/Lag) | 1000 | 680 | 613 | 67 | 67000 | 0.067 | 25959 | 25889 | 70 | 70000 | 0.07
3 | KIRBY PLACE-1 | 4864846 | ELSTER | Kvarh(Lead/Lag) | 1000 | 1714 | 1522 | 192 | 192000 | 0.192 | 33803 | 33708 | 95 | 95000 | 0.095
4 | KIRBY PLACE-2 | 4864847 | ELSTER | Kvarh(Lead/Lag) | 1000 | 919 | 927 | -8 | -8000 | -0.008 | 18332 | 18339 | -7 | -7000 | -0.007
5 | SHEKHAWATI- 1 | 4864850 | ELSTER | Kvarh(Lead/Lag) | 1000 | 3630 | 3567 | 63 | 63000 | 0.063 | 10168 | 10167 | 1 | 1000 | 0.001
6 | SHEKHAWATI- 2 | 4864900 | ELSTER | Kvarh(Lead/Lag) | -500 | 10757 | 11001 | -244 | 122000 | 0.122 | 58534 | 58534 | 0 | 0 | 0 | Reverse Polarity
RIDGE VALLEY ON 33KV
7 | KHBR LANE-1 -EXP | 4864804 | ELSTER | Kvarh(Lead/Lag) | 100 | 997066 | 997370 | -304 | -30400 | -0.0304 | 999978 | 999978 | 0 | 0 | 0
8 | KHBR LANE-2 -EXP. | 4865163 | ELSTER | Kvarh(Lead/Lag) | 100 | 996724 | 996770 | -46 | -4600 | -0.0046 | 999920 | 999920 | 0 | 0 | 0
| TOTAL FED FROM DTL SYSTEM. | [8 empty] | 0.497 |  |  |  |  | 0.289
FED FROM BSES RAJDHANI POWER LIMITED (11KV)
9 | SIGNAL ENCLAVE | 4865065 | ELSTER | Kvarh(Lead/Lag) | 100 | 3437 | 3437 | 0 | 0 | 0 | 34364 | 34364 | 0 | 0 | 0
10 | R.R. HOSPITAL | 4865066 | ELSTER | Kvarh(Lead/Lag) | 100 | 45584 | 45445 | 139 | 13900 | 0.0139 | 71775 | 71666 | 109 | 10900 | 0.0109
11 | DEFENCE CLUB | 4865067 | ELSTER | Kvarh(Lead/Lag) | 100 | 72568 | 72403 | 165 | 16500 | 0.0165 | 11074 | 11074 | 0 | 0 | 0
12 | SUBROTO PARK | 4865078 | ELSTER | Kvarh(Lead/Lag) | 100 | 42432 | 41394 | 1038 | 103800 | 0.1038 | 59758 | 59529 | 229 | 22900 | 0.0229
13 | SUBROTO PARK | 4865079 | ELSTER | Kvarh(Lead/Lag) | 100 | 999989 | 999989 | 0 | 0 | 0 | 20273 | 20273 | 0 | 0 | 0
14 | BI LINES | 4865080 | ELSTER | Kvarh(Lead/Lag) | 100 | 82778 | 81969 | 809 | 80900 | 0.0809 | 58179 | 58136 | 43 | 4300 | 0.0043
15 | BI LINES | 4865075 | ELSTER | Kvarh(Lead/Lag) | 100 | 5659 | 5267 | 392 | 39200 | 0.0392 | 1801 | 1759 | 42 | 4200 | 0.0042
TOTAL FED FROM BSES RAJDHANI POWER LIMITED (11KV) | [9 empty] | 0.2151 |  |  |  |  | 0.0381
MES(-)
FED TO BSES RAJDHANI POWER LIMITED (11KV)
16 | BOOSTER PUMP | 4902545 | ELSTER | Kvarh(Lead/Lag) | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL FED TO BSES RAJDHANI POWER LIMITED (11KV) | [9 empty] | 0 |  |  |  |  | 0
| TOTAL FED FROM BSES RAJDHANI POWER LIMITED (11KV) | [8 empty] | 0.2151 |  |  |  |  | 0.0381
| TOTAL FED FROM DTL SYSTEM. | [8 empty] | 0.497 |  |  |  |  | 0.289
| GRAND TOTAL (BSES RPL+NDPL+DTL) | [8 empty] | 0.7121 |  |  |  |  | 0.3271
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | 0.7121 | (REACTIVE MUs) |  |  |  | 0.3271 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | 0.0087256 | (REACTIVE MUs) |  |  |  | -0.075535 | (REACTIVE MUs)
[9 empty] | TOTAL | 0.72083 | (REACTIVE MUs) |  |  |  | 0.25156 | (REACTIVE MUs)

## ROHTAK ROAD
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | DECEMBER-2013
ROHTAK ROAD
[8 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
TO BSES RAJDHANI
AT 33 KV LEVEL
1 | O/G SBMILL-1 | 4864796 | ELSTER | Kvarh(Lead/Lag) | 100 | 42230 | 44325 | -2095 | -209500 | -0.2095 | 79302 | 79296 | 6 | 600 | 0.0006
2 | O/G SBMILL-2 | 4864797 | ELSTER | Kvarh(Lead/Lag) | 100 | 994865 | 996916 | -2051 | -205100 | -0.2051 | 999021 | 999177 | -156 | -15600 | -0.0156
3 | O/G VISHAL-1 | 4864818 | ELSTER | Kvarh(Lead/Lag) | 100 | 248148 | 242401 | 5747 | 574700 | 0.5747 | 98273 | 98151 | 122 | 12200 | 0.0122
4 | O/G MADI PUR | 4864842 | ELSTER | Kvarh(Lead/Lag) | 937.5 | 30259 | 29701 | 558 | 523125 | 0.52312 | 18468 | 18447 | 21 | 19687.5 | 0.019688
AT 33/11 KV LEVEL
5 | TX.-I | 4864880 | ELSTER | Kvarh(Lead/Lag) | -500 | 985708 | 985970 | -262 | 131000 | 0.131 | 925169 | 925449 | -280 | 140000 | 0.14
6 | TX-II | 4864881 | ELSTER | Kvarh(Lead/Lag) | -500 | 989616 | 989674 | -58 | 29000 | 0.029 | 980448 | 980901 | -453 | 226500 | 0.2265
7 | B/C (IMP.TO BRPL) | 4902572 | ELSTER | Kvarh(Lead/Lag) | 300 | 17 | 17 | 0 | 0 | 0 | 999996 | 1000000 | -4 | -1200 | -0.0012
| TOTAL BSES RAJDHANI PO.LTD. | [8 empty] | 0.84323 |  |  |  |  | 0.38219
TO BSES YAMUNA PO. LTD.
AT 33 KV LEVEL
8 | O/G FAIZ ROAD | 4864794 | ELSTER | Kvarh(Lead/Lag) | 200 | 932905 | 934977 | -2072 | -414400 | -0.4144 | 991739 | 991753 | -14 | -2800 | -0.0028
9 | O/G DMS | 4864932 | ELSTER | Kvarh(Lead/Lag) | 200 | 995192 | 997889 | -2697 | -539400 | -0.5394 | 105 | 0 | 105 | 21000 | 0.021
| TOTAL (BSES Y.P.L.) | [8 empty] | -0.9538 |  |  |  |  | 0.0182
TO NORTH DELHI POWER LIMITED
AT 33 KV LEVEL
10 | O/G VISHAL-2 | 4864819 | ELSTER | Kvarh(Lead/Lag) | 200 | 228152 | 225880 | 2272 | 454400 | 0.4544 | 263868 | 263805 | 63 | 12600 | 0.0126
11 | O/G 33KV RAMPURA-1 | 4864801 | ELSTER | Kvarh(Lead/Lag) | 200 | 101141 | 99327 | 1814 | 362800 | 0.3628 | 41520 | 41507 | 13 | 2600 | 0.0026
12 | O/G 33KV RAMPURA-2 | 4864820 | ELSTER | Kvarh(Lead/Lag) | 100 | 162312 | 158568 | 3744 | 374400 | 0.3744 | 72424 | 72389 | 35 | 3500 | 0.0035
13 | O/G 33KV SH.W.BAGH-I | 4865168 | ELSTER | Kvarh(Lead/Lag) | 1000 | 989897 | 989785 | 112 | 112000 | 0.112 | 998410 | 998402 | 8 | 8000 | 0.008
14 | O/G 33KV SH.W.BAGH-2 | 4864802 | ELSTER | Kvarh(Lead/Lag) | 100 | 966358 | 967379 | -1021 | -102100 | -0.1021 | 7143 | 7159 | -16 | -1600 | -0.0016
15 | O/G 33KV KIRTI NAGAR | 5128400 | ELSTER | Kvarh(Lead/Lag) | 937.5 | 999368 | 999399 | -31 | -29062.5 | -0.029063 | 999855 | 1000003 | -148 | -138750 | -0.13875
AT 33/11 KV LEVEL
16 | TX-III | 4864882 | ELSTER | Kvarh(Lead/Lag) | -625 | 987674 | 988032 | -358 | 223750 | 0.22375 | 995542 | 995547 | -5 | 3125 | 0.003125
17 | B/C (IMP.TO NDPL) | 4902572 | ELSTER | Kvarh(Lead/Lag) | -300 | 17 | 17 | 0 | 0 | 0 | 999996 | 1000001 | -5 | 1500 | 0.0015
| TOTAL NDPL | [8 empty] | 1.3962 |  |  |  |  | -0.10903
| E) NET EXPORT TO BSES RPL | [8 empty] | 0.84323 |  |  |  |  | 0.38219
| F) NET EXPORT TO BSES YPL | [8 empty] | -0.9538 |  |  |  |  | 0.0182
| G) NET EXPORT TO N.D.P.L. | [8 empty] | 1.3962 |  |  |  |  | -0.10903

## STEPPED UP GENCO
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | DECEMBER-2013
A.) EXPORT/IMPORT OF REACTIVE ENERGY IN LEAD/LAG MODE ON IBT's AT GENCO
[8 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | REMARK
G.T.
| (66KV ) | (EXPORT)
1 | IBT-I | 4865001 | ELSTER | kvarh (Lead/lag) | 2000 | 1055 | 476 | 579 | 1158000 | 1.158 | 406 | 31 | 375 | 750000 | 0.75
2 | IBT-2 | 4902498 | ELSTER | kvarh (Lead/lag) | 2000 | 13097 | 12794 | 303 | 606000 | 0.606 | 2242 | 2363 | -121 | -242000 | -0.242
[7 empty] | NET REACTIVE ENERGY |  |  | 1.764 |  | NET REACTIVE ENERGY |  |  | 0.508
RPH
| (33KV ) | (EXPORT)
3 | IBT-I | 4902505 | ELSTER | kvarh (Lead/lag) | 1000 | 993312 | 993241 | 71 | 71000 | 0.071 | 39613 | 39638 | -25 | -25000 | -0.025
4 | IBT-2 | 5128424 | ELSTER | kvarh (Lead/lag) | 1000 | 996230 | 996079 | 151 | 151000 | 0.151 | 994062 | 994780 | -718 | -718000 | -0.718
[7 empty] | NET REACTIVE ENERGY |  |  | 0.222 |  | NET REACTIVE ENERGY |  |  | -0.743
1)TOTAL NET REACTIVE ENERGY FROM GENCO AT 66/33KV LEVEL | [9 empty] | 1.986 |  |  |  |  | -0.235
B) | REACTIVE ENERGY DRAWL ON FEEDERS FROM GENCO BY
[7 empty] | NDPL = |  |  | 0 |  |  |  |  | 0
[7 empty] | BRPL = |  |  | 0 |  |  |  |  | 0
[7 empty] | BYPL = |  |  | -0.7138 |  |  |  |  | -8.8574
[7 empty] | NDMC = |  |  | -0.363 |  |  |  |  | 1.2217
MES =
[7 empty] | 2)TOTAL |  |  | -1.0768 |  |  |  |  | -7.6357
C) TOTAL REACTIVE ENERGY TO BE DISTRIBUTED AMONGS DISCOMs [1+2]= | [9 empty] | 0.9092 |  |  |  |  | -7.8707
D). | SHARE OF EACH DISCOM TO BE DISTRIBUTED ON PROPORTION TO THEIR ACTIVE ENERGY DRAWAL OF C
1) | NDPL | (ACTIVE ENERGY DRAWL= |  |  |  | 30.5102 | % |  |  | 0.2774 |  |  |  |  | -2.4014
2) | BRPL | (ACTIVE ENERGY DRAWL= |  |  |  | 40.3086 | % |  |  | 0.36649 |  |  |  |  | -3.1726
3) | BYPL | (ACTIVE ENERGY DRAWL= |  |  |  | 23.2904 | % |  |  | 0.21176 |  |  |  |  | -1.8331
4) | NDMC | (ACTIVE ENERGY DRAWL= |  |  |  | 4.9311 | % |  |  | 0.044834 |  |  |  |  | -0.38811
5) | MES | (ACTIVE ENERGY DRAWL= |  |  |  | 0.9597 | % |  |  | 0.0087256 |  |  |  |  | -0.075535
Note :Sharing taken from wk-36 abt bill 2013-14

## FINAL EX. SUMMARY
DELHI TRANSCO LIMITED
REACTIVE ENERGY RELEASE STATEMENT TO LICENSEES.
PERIOD 1st DECEMBER-2013 TO 31ST DECEMBER-2013
FINAL EXECUTIVE SUMMERY
[6 empty] | Energy for above 103% |  | Energy for below 97%
1 | NET REACTIVE ENERGY TO N.D.P.L. |  |  |  | + | 0.25465 |  | -2.0841
2 | NET REACTIVE ENERGY TO BSES RAJDHANI PO.LTD. |  |  |  |  | -6.7751 |  | -1.2435
3 | NET REACTIVE ENERGY TO BSES YAMUNA PO.LTD. |  |  |  | + | 5.2134 |  | -9.0809
4 | NET REACTIVE ENERGY TO NDMC |  |  |  | + | 2.8174 | + | 2.8311
5 | NET REACTIVE ENERGY TO MES |  |  |  | + | 0.72083 | + | 0.25156
ALL FIGURES IN Mus.
Note:-
+ve sign indicates reactive energy drawl from the grid/system
-ve sign indicates reactive energy injected to the grid/system

## PRAGATI
[8 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 01/01/2014 | INTIAL READING 01/12/2013 | DIFF. | CONSP. | REACTIVE MUs
PRAGATI
| (220 KV) | (EXPORT)
1 | GT-I | 4902492 | ELSTER | kvarh (lag) | 1500 | 957896 | 958415 | -519 | -778500 | -0.7785 | 981015 | 981015 | 0 | 0 | 0
2 | GT-II | 5128477 | ELSTER | kvarh (lag) | 1500 | 997920 | 998180 | -260 | -390000 | -0.39 | 995977 | 995979 | -2 | -3000 | -0.003
3 | STG-III | 4902494 | ELSTER | kvarh (lag) | 1500 | 910368 | 911662 | -1294 | -1941000 | -1.941 | 966279 | 966279 | 0 | 0 | 0
[8 empty] | NET REACTIVE ENERGY |  | -3.1095 |  |  | NET REACTIVE ENERGY |  | -0.003
I.P.STATION
| (33KV) | (EXPORT)
1 | IBT-I | 4902509 | ELSTER | kvarh (lag) | 5000 | 997786 | 997689 | 97 | 485000 | 0.485 | 31064 | 31059 | 5 | 25000 | 0.025
2 | IBT-2 | 4902510 | ELSTER | kvarh (lag) | 1000 | 999668 | 999635 | 33 | 33000 | 0.033 | 3099 | 3196 | -97 | -97000 | -0.097
3 | IBT-3 | 4864947 | ELSTER | kvarh (lag) | 1000 | 971815 | 970801 | 1014 | 1014000 | 1.014 | 990180 | 990105 | 75 | 75000 | 0.075
[8 empty] | NET REACTIVE ENERGY |  | 1.532 |  |  | NET REACTIVE ENERGY |  | 0.003