## NDPL
DELHI TRANSCO LIMITED | [15 empty] | NOVEMBER-2023
REACTIVE ENERGY CONSUMPTION STATEMENT
Customer:NORTH DELHI POWER LIMITED.
NDPL(+) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
GOPAL PUR
1 | Tx.1 | 4902497 | ELSTER | Kvarh(Lead/Lag) | -1000 | 369 | 369 | 0 | 0 | 0 | 998359 | 998311 | 48 | -48000 | -0.048
2 | TX.2 | 4864976 | ELSTER | Kvarh(Lead/Lag) | -2000 | 99976 | 99612 | 364 | -728000 | -0.728 | 5118 | 5118 | 0 | 0 | 0
|  | Q0491811 | Secure | Kvarh(Lead/Lag) | -1 | 1559000 | 1266000 | 293000 | -293000 | -0.293 | -9000 | -9000 | 0 | 0 | 0
3 | Tx.3 | 4864924 | ELSTER | Kvarh(Lead/Lag) | -1000 | 18618 | 18506 | 112 | -112000 | -0.112 | 2523 | 2522 | 1 | -1000 | -0.001 | loaded upto 24.11.23
4 | Tx.4 | Q0491809 | Secure | Kvarh(Lead/Lag) | -1 | 2104000 | 1756000 | 348000 | -348000 | -0.348 | -111000 | -111000 | 0 | 0 | 0
SUBZI MANDI
5 | Tx.1 | 4865012 | ELSTER | Kvarh(Lead/Lag) | -1000 | 174 | 129 | 45 | -45000 | -0.045 | 9 | 5 | 4 | -4000 | -0.004
6 | Tx.2 | 4864896 | ELSTER | Kvarh(Lead/Lag) | -2000 | 318 | 305 | 13 | -26000 | -0.026 | 1233 | 1169 | 64 | -128000 | -0.128
ROHINI
7 | Tx 1 | 4864964 | ELSTER | Kvarh(Lead/Lag) | -1000 | 37591 | 35983 | 1608 | -1608000 | -1.608 | 999052 | 999052 | 0 | 0 | 0
8 | Tx.2 | 4865022 | ELSTER | Kvarh(Lead/Lag) | -1000 | 46970 | 45380 | 1590 | -1590000 | -1.59 | 997321 | 997321 | 0 | 0 | 0
9 | Tx.-3 | 4864997 | ELSTER | Kvarh(Lead/Lag) | -1000 | 33680 | 31854 | 1826 | -1826000 | -1.826 | 996853 | 996853 | 0 | 0 | 0
10 | Tx.-4 | 5295166 | ELSTER | Kvarh(Lead/Lag) | -500 | 15827 | 13765 | 2062 | -1031000 | -1.031 | 812614 | 812614 | 0 | 0 | 0
SHALIMAR BAGH
11 | Tx.1 | 4864930 | ELSTER | Kvarh(Lead/Lag) | -1000 | 13941 | 12863 | 1078 | -1078000 | -1.078 | 998522 | 998522 | 0 | 0 | 0
12 | Tx.-2 | 4864917 | ELSTER | Kvarh(Lead/Lag) | -1000 | 36768 | 34792 | 1976 | -1976000 | -1.976 | 133 | 128 | 5 | -5000 | -0.005
13 | Tx.-3 | 4864922 | ELSTER | Kvarh(Lead/Lag) | -1000 | 64731 | 64419 | 312 | -312000 | -0.312 | 995663 | 995663 | 0 | 0 | 0
14 | Tx.-4 | 40001535 | ELSTER | Kvarh(Lead/Lag) | -1 | 30877 | 30877 | 0 | 0 | 0 | 99999712 | 99999712 | 0 | 0 | 0
15 | 220KV DMRC-1 | 4902494 | ELSTER | Kvarh(Lead/Lag) | 1000 | 667633 | 673897 | -6264 | -6264000 | -6.264 | 999743 | 999743 | 0 | 0 | 0
16 | 220KV DMRC-2 | 4902484 | ELSTER | Kvarh(Lead/Lag) | 500 | 687091 | 693108 | -6017 | -3008500 | -3.0085 | 999974 | 999974 | 0 | 0 | 0
NARELA
17 | Tx.1 | 4864963 | ELSTER | Kvarh(Lead/Lag) | -1000 | 16027 | 15987 | 40 | -40000 | -0.04 | 175 | 23 | 152 | -152000 | -0.152
18 | Tx.2 | 4865043 | ELSTER | Kvarh(Lead/Lag) | -1000 | 6 | 6 | 0 | 0 | 0 | 7779 | 6928 | 851 | -851000 | -0.851
19 | Tx.3 | 4865052 | ELSTER | Kvarh(Lead/Lag) | -1000 | 63188 | 62920 | 268 | -268000 | -0.268 | 2071 | 2051 | 20 | -20000 | -0.02
NARAINA
20 | O/G REWARI LINE 1(payal) | 4864836 | ELSTER | Kvarh(Lead/Lag) | 1000 | 998581 | 998581 | 0 | 0 | 0 | 985523 | 985538 | -15 | -15000 | -0.015
21 | O/G REWARI LINE 2 | 4865182 | ELSTER | Kvarh(Lead/Lag) | 4000 | 999550 | 999551 | -1 | -4000 | -0.004 | 999531 | 999533 | -2 | -8000 | -0.008
22 | 16 MVA TX.-1 | 4864880 | ELSTER | Kvarh(Lead/Lag) | 500 | 1996 | 2012 | -16 | -8000 | -0.008 | 17362 | 17360 | 2 | 1000 | 0.001
23 | 16 MVA TX.-2 | 4864860 | ELSTER | Kvarh(Lead/Lag) | 500 | 11264 | 11140 | 124 | 62000 | 0.062 | 31165 | 31164 | 1 | 500 | 0.0005
24 | INDER PURI | 4864865 | ELSTER | Kvarh(Lead/Lag) | 1000 | 998289 | 998363 | -74 | -74000 | -0.074 | 991983 | 991988 | -5 | -5000 | -0.005
25 | INDER PURI-2 | 4865117 | ELSTER | Kvarh(Lead/Lag) | 1333.333 | 999992 | 999992 | 0 | 0 | 0 | 993397 | 993405 | -8 | -10666.664 | -0.010667
26 | Pandav Nagar | 4864846 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999752 | 999754 | -2 | -2000 | -0.002 | 15 | 23 | -8 | -8000 | -0.008
KASHMIRI GATE
27 | 220 kV DMRC #1 | 5128479 | ELSTER | Kvarh(Lead/Lag) | 1000 | 998612 | 999537 | -925 | -925000 | -0.925 | 31 | 31 | 0 | 0 | 0
28 | 220 kV DMRC #2 | 4902482 | ELSTER | Kvarh(Lead/Lag) | 500 | 878590 | 881265 | -2675 | -1337500 | -1.3375 | 999216 | 999216 | 0 | 0 | 0
29 | CIVIL LINE | 4864791 | ELSTER | Kvarh(Lead/Lag) | 266.67 | 990628 | 990655 | -27 | -7200.09 | -0.0072001 | 999964 | 999962 | 2 | 533.34 | 0.00053334
30 | CIVIL LINE-2 | 4865184 | ELSTER | Kvarh(Lead/Lag) | 2000 | 6 | 6 | 0 | 0 | 0 | 80 | 70 | 10 | 20000 | 0.02
KANJAWALA
31 | TX-1 | 4865041 | ELSTER | Kvarh(Lead/Lag) | -1000 | 60976 | 60876 | 100 | -100000 | -0.1 | 995026 | 995015 | 11 | -11000 | -0.011
32 | Tx.2 | 4902499 | ELSTER | Kvarh(Lead/Lag) | -1000 | 6069 | 5876 | 193 | -193000 | -0.193 | 999744 | 999737 | 7 | -7000 | -0.007
33 | Tx.3 | 4864788 | ELSTER | Kvarh(Lead/Lag) | -2000 | 42456 | 41360 | 1096 | -2192000 | -2.192 | 999690 | 999690 | 0 | 0 | 0
BAWANA
34 | I/C 100 MVA PR.TR. | 4864847 | ELSTER | Kvarh(Lead/Lag) | -2500 | 1158 | 272 | 886 | -2215000 | -2.215 | 0 | 0 | 0 | 0 | 0
DSIDC BAWANA
35 | 66KV TX.1 | 4864892 | ELSTER | Kvarh(Lead/Lag) | -4000 | 18155 | 17173 | 982 | -3928000 | -3.928 | 68 | 66 | 2 | -8000 | -0.008
36 | 66KV TX.2 | 4864992 | ELSTER | Kvarh(Lead/Lag) | -1000 | 179134 | 177545 | 1589 | -1589000 | -1.589 | 998443 | 998440 | 3 | -3000 | -0.003
37 | 66KV TX.3 | 4864827 | ELSTER | Kvarh(Lead/Lag) | -333.33 | 423327 | 414437 | 8890 | -2963303.7 | -2.9633 | 1536 | 1536 | 0 | 0 | 0
38 | 66KV TX.4 | 5128449 | ELSTER | Kvarh(Lead/Lag) | -2000 | 59603 | 57512 | 2091 | -4182000 | -4.182 | 132 | 132 | 0 | 0 | 0
ROHINI-II
38 | Tx.1 | 4864957 | ELSTER | Kvarh(Lead/Lag) | -2500 | 5282 | 4426 | 856 | -2140000 | -2.14 | 92 | 92 | 0 | 0 | 0
39 | Tx.2 | 5128468 | ELSTER | Kvarh(Lead/Lag) | -1000 | 167354 | 165044 | 2310 | -2310000 | -2.31 | 2528 | 2528 | 0 | 0 | 0
SGTN
40 | Tx.1 | XF465246 | Secure | Kvarh(Lead/Lag) | -1 | 19220000 | 17401000 | 1819000 | -1819000 | -1.819 | 5005000 | 5005000 | 0 | 0 | 0 | INITIAL DATA 31.10.2023
41 | Tx.2 | XF465248 | Secure | Kvarh(Lead/Lag) | -1 | 58277000 | 54324000 | 3953000 | -3953000 | -3.953 | 3268000 | 3268000 | 0 | 0 | 0 | INITIAL DATA 31.10.2023
WAZIRPUR
42 | Tx.1 | 4864903 | ELSTER | Kvarh(Lead/Lag) | -1000 | 48147 | 45119 | 3028 | -3028000 | -3.028 | 998002 | 998002 | 0 | 0 | 0
43 | Tx.2 | 4864946 | ELSTER | Kvarh(Lead/Lag) | -1000 | 61821 | 61641 | 180 | -180000 | -0.18 | 885 | 885 | 0 | 0 | 0
EXPORT TO EAST & CENTRE IMPORTS
SHASTRI PARK
44 | PUSA GRID-I | 4864843 | ELSTER | Kvarh(Lead/Lag) | 1000 | 993009 | 993365 | -356 | -356000 | -0.356 | 24322 | 24322 | 0 | 0 | 0
[6 empty] | #N/A | #N/A |  |  |  | #N/A | #N/A
| NDPL(+) continue | [14 empty] | NOVEMBER-2023
DMS
45 | 33KV PANDAV NGR | 4902578 | ELSTER | Kvarh(Lead/Lag) | 300 | 998507 | 998507 | 0 | 0 | 0 | 999767 | 999767 | 0 | 0 | 0
VISHAL
46 | RAMESH NAGAR-1 | 4865065 | ELSTER | Kvarh(Lead/Lag) | 266.67 | 0 | 0 | 0 | 0 | 0 | 999995 | 999995 | 0 | 0 | 0
47 | BALI NAGAR -1 | 4902541 | ELSTER | Kvarh(Lead/Lag) | 100 | 999482 | 999482 | 0 | 0 | 0 | 999486 | 999486 | 0 | 0 | 0
48 | ESI HOSPITAL | 4902539 | ELSTER | Kvarh(Lead/Lag) | 100 | 3156 | 3231 | -75 | -7500 | -0.0075 | 35655 | 35650 | 5 | 500 | 0.0005
S.B.MILL
49 | MOTI NAGAR KIOSK | 4902591 | ELSTER | Kvarh(Lead/Lag) | 1333 | 746 | 746 | 0 | 0 | 0 | 634 | 641 | -7 | -9331 | -0.009331
50 | 53 RAMA ROAD | 4902528 | ELSTER | Kvarh(Lead/Lag) | 100 | 298 | 298 | 0 | 0 | 0 | 4664 | 4664 | 0 | 0 | 0
51 | BREAK FAST | 4902523 | ELSTER | Kvarh(Lead/Lag) | 100 | 999815 | 999815 | 0 | 0 | 0 | 999943 | 999943 | 0 | 0 | 0
52 | 70 RAMA ROAD | 4865093 | ELSTER | Kvarh(Lead/Lag) | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | MOTI NAGAR 2 | 4902548 | ELSTER | Kvarh(Lead/Lag) | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | NAJAFGARH ROAD | 4902564 | ELSTER | Kvarh(Lead/Lag) | 100 | 1616 | 1616 | 0 | 0 | 0 | 12625 | 12291 | 334 | 33400 | 0.0334
B.G.ROAD
55 | CSA | 4902519 | ELSTER | Kvarh(Lead/Lag) | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | DCM NO.1 | 4902579 | ELSTER | Kvarh(Lead/Lag) | 500 | 999859 | 999859 | 0 | 0 | 0 | 2500 | 2479 | 21 | 10500 | 0.0105
57 | DCM NO.2 | 4865089 | ELSTER | Kvarh(Lead/Lag) | 500 | 999982 | 999982 | 0 | 0 | 0 | 7 | 30 | -23 | -11500 | -0.0115
58 | SADAR S/S | 4865090 | ELSTER | Kvarh(Lead/Lag) | 500 | 1202 | 1202 | 0 | 0 | 0 | 1703 | 1674 | 29 | 14500 | 0.0145
D.M.S.
59 | PHILIPS | 4902568 | ELSTER | Kvarh(Lead/Lag) | 100 | 992598 | 992656 | -58 | -5800 | -0.0058 | 3862 | 3760 | 102 | 10200 | 0.0102
FAIZ ROAD
60 | TIBIA COLLEGE-1 | 4902599 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 33 | 32 | 1 | 1333.33 | 0.0013333 | 86 | 79 | 7 | 9333.31 | 0.0093333
61 | TIBIA COLLEGE-2 | 4902520 | ELSTER | Kvarh(Lead/Lag) | 100 | 20132 | 20096 | 36 | 3600 | 0.0036 | 6672 | 6668 | 4 | 400 | 0.0004 | Data upto 06-11-23
[10 empty] | 0.0044 |  |  |  |  | 0.0004 | Assessment(06.11.23 To 21.11.23)
|  | 4865082 | ELSTER | Kvarh(Lead/Lag) | 133.33 | 6 | 0 | 6 | 799.98 | 0.00079998 | 0 | 0 | 0 | 0 | 0 | w.e.f 21-11-2023
62 | MANAK PURA | 4902577 | ELSTER | Kvarh(Lead/Lag) | 100 | 2735 | 2605 | 130 | 13000 | 0.013 | 238 | 230 | 8 | 800 | 0.0008
KASHMIRI GATE
63 | 20MVA TX. | 4864797 | ELSTER | Kvarh(Lead/Lag) | 100 | 60625 | 60902 | -277 | -27700 | -0.0277 | 2652 | 2652 | 0 | 0 | 0
64 | FLYOVER | 4865074 | ELSTER | Kvarh(Lead/Lag) | 133.33 | 432 | 432 | 0 | 0 | 0 | 1215 | 1215 | 0 | 0 | 0
65 | B/C (IMP. TO NDPL) | 4902585 | ELSTER | Kvarh(Lead/Lag) | -400 | 999998 | 999998 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0
REWARI LINE (11KV TRANSFER OF ENERGY)
66 | BSES -NDPL(EX.) ON BUS-1&2 | 4902529 | ELSTER | Kvarh(Lead/Lag) | -400 | 999999 | 999999 | 0 | 0 | 0 | 999999 | 999999 | 0 | 0 | 0
67 | BSES -NDPL(EX.) ON BUS-2&3 | 4902525 | ELSTER | Kvarh(Lead/Lag) | 400 | 999895 | 999895 | 0 | 0 | 0 | 999460 | 999460 | 0 | 0 | 0
MUNDKA
68 | 66KV MANGOL PURI | 4864983 | ELSTER | Kvarh(Lead/Lag) | 800 | 930143 | 931125 | -982 | -785600 | -0.7856 | 999689 | 999689 | 0 | 0 | 0
69 | GHEWARA | 4865032 | ELSTER | Kvarh(Lead/Lag) | 800 | 992984 | 993307 | -323 | -258400 | -0.2584 | 999999 | 999999 | 0 | 0 | 0
PEERAGARHI
70 | SUDARSHAN PARK(L -1) | 4864810 | ELSTER | Kvarh(Lead/Lag) | 200 | 956935 | 957071 | -136 | -27200 | -0.0272 | 2319 | 2313 | 6 | 1200 | 0.0012
71 | RANI BAGH(L-2) | 4864901 | ELSTER | Kvarh(Lead/Lag) | 250 | 988261 | 988346 | -85 | -21250 | -0.02125 | 958 | 957 | 1 | 250 | 0.00025
REWARI LINE
72 | PPK-1 | 4864960 | ELSTER | Kvarh(Lead/Lag) | 1000 | 978018 | 979079 | -1061 | -1061000 | -1.061 | 1762 | 1762 | 0 | 0 | 0
73 | SAGARPUR | 5129960 | ELSTER | Kvarh(Lead/Lag) | 281.25 | 999557 | 999566 | -9 | -2531.25 | -0.0025313 | 430 | 430 | 0 | 0 | 0
DEV NAGAR
74 | 33KV RAMA ROAD | Q0487625 | Secure | Kvarh(Lead/Lag) | 1 | -510000 | -364000 | -146000 | -146000 | -0.146 | 0 | 0 | 0 | 0 | 0
75 | 33KV SHAHZADA BAGH | Q0487626 | Secure | Kvarh(Lead/Lag) | 1 | 615000 | 961000 | -346000 | -346000 | -0.346 | 0 | 0 | 0 | 0 | 0
76 | 33KV NARAINA DTC CKT-II | Q0487631 | Secure | Kvarh(Lead/Lag) | 1 | -301000 | 0 | -301000 | -301000 | -0.301 | 0 | 0 | 0 | 0 | 0 | w.e.f 08-11-2023
| ENERGY INPUT AT 66/33/11 KV LEVEL | [8 empty] | -56.9644 |  |  |  |  | -1.202
NDPL(-) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 % |  |  | NOVEMBER-2023
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
NARAINA
1 | GOPI NATH BAZAAR | 4902566 | ELSTER | Kvarh(Lead/Lag) | -100 | 679 | 680 | -1 | 100 | 0.0001 | 3666 | 3573 | 93 | -9300 | -0.0093
MANGOLPURI
2 | NANGLOI-2 EXP | Y0357821 | Secure | Kvarh(Lead/Lag) | -0.8 | 761000 | 713000 | 48000 | -38400 | -0.0384 | 9000 | 9000 | 0 | 0 | 0
SUBZI MANDI
3 | O/G BG Rd.1 | 4864899 | ELSTER | Kvarh(Lead/Lag) | -500 | 973179 | 973189 | -10 | 5000 | 0.005 | 992117 | 992116 | 1 | -500 | -0.0005
4 | O/G BG Rd.2 | 4864825 | ELSTER | Kvarh(Lead/Lag) | -133.33 | 7747 | 7978 | -231 | 30799.23 | 0.030799 | 8370 | 8370 | 0 | 0 | 0
SUDARSHAN PARK
5 | VISHAL (EXP) | 4865149 | ELSTER | Kvarh(Lead/Lag) | -187.5 | 995887 | 996030 | -143 | 26812.5 | 0.026812 | 998246 | 998248 | -2 | 375 | 0.000375
KANJAWALA
6 | 66KV DMRC | Y0357713 | ELSTER | Kvarh(Lead/Lag) | -0.4 | -1067000 | -1052000 | -15000 | 6000 | 0.006 | -680000 | -37000 | -643000 | 257200 | 0.2572
MUNDKA
7 | 66KV NGL. T-OFF MGL P | 4864971 | ELSTER | Kvarh(Lead/Lag) | 800 | 0 | 0 | 0 | 0 | 0 | 999495 | 999495 | 0 | 0 | 0
NARELA (RAILWAY CKTS)
8 | 66KV RLY Ckt-1 | 4864952 | ELSTER | Kvarh(Lead/Lag) | -625 | 992095 | 992000 | 95 | -59375 | -0.059375 | 1346 | 1343 | 3 | -1875 | -0.001875
9 | 66KV RLY Ckt-1 | 4865039 | ELSTER | Kvarh(Lead/Lag) | -500 | 999688 | 999716 | -28 | 14000 | 0.014 | 801 | 796 | 5 | -2500 | -0.0025
REWARI LINE
10 | VISHAL-1 | [8 empty] | 0.0374 |  |  |  |  | 0 | Assessment(01.11.23 To 09.11.23)
|  | 4902510 | ELSTER | Kvarh(Lead/Lag) | -400 | 999743 | 1000000 | -257 | 102800 | 0.1028 | 0 | 0 | 0 | 0 | 0 | w.e.f 09.11.2023
11 | VISHAL-2 | 4865140 | ELSTER | Kvarh(Lead/Lag) | -937.5 | 999825 | 999963 | -138 | 129375 | 0.12937 | 999739 | 999740 | -1 | 937.5 | 0.0009375
12 | MAYAPURI | 4864808 | ELSTER | Kvarh(Lead/Lag) | -187.5 | 980278 | 980806 | -528 | 99000 | 0.099 | 2532 | 2533 | -1 | 187.5 | 0.0001875
13 | 20MVATX-III | 4865080 | ELSTER | Kvarh(Lead/Lag) | -2500 | 999982 | 999999 | -17 | 42500 | 0.0425 | 999997 | 999997 | 0 | 0 | 0
14 | 16MVA TX-1 | 4864822 | ELSTER | Kvarh(Lead/Lag) | -100 | 993010 | 993052 | -42 | 4200 | 0.0042 | 32214 | 32214 | 0 | 0 | 0
| TOTAL OF INTER COMPANY EXCHANGE POINTS | [8 empty] | 0.40021 |  |  |  |  | 0.24453
EXECUTIVE SUMMERY N.D.P.L.
1) ENERGY RELEASED AT 66/33/11 KV LEVEL (Refer sheet NDPL(+)) | [9 empty] | -56.9644 |  |  |  |  | -1.202
2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer sheet NDPL(-)) | [9 empty] | 0.40021 |  |  |  |  | 0.24453
3) FROM ROHTAK ROAD (REFER ENERGY BALANCE SHEET ROHTAK ROAD ENCL) | [9 empty] | -2.8749 |  |  |  |  | -0.000875
NET ENERGY TO NORTH DELHI POWER LIMITED | [9 empty] | -59.439 |  |  |  |  | -0.95833
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | -59.439 | (REACTIVE MUs) |  |  |  | -0.95833 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | 7.107 | (REACTIVE MUs) |  |  |  | 0.014632 | (REACTIVE MUs)
[9 empty] | TOTAL | -52.332 | (REACTIVE MUs) |  |  |  | -0.9437 | (REACTIVE MUs)

## BRPL
DELHI TRANSCO LIMITED | [14 empty] | NOVEMBER-2023
REACTIVE ENERGY CONSUMPTION STATEMENT
CUSTOMER-BSES RAJDHANI POWER LIMITED
BRPL (+) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
I.P.STATION
1 | BAY-24 | 4865170 | ELSTER | Kvarh(Lead/Lag) | 1000 | 997803 | 997803 | 0 | 0 | 0 | 987330 | 987652 | -322 | -322000 | -0.322
2 | BAY-25 | 4864887 | ELSTER | Kvarh(Lead/Lag) | 1000 | 998503 | 998503 | 0 | 0 | 0 | 997850 | 998030 | -180 | -180000 | -0.18
3 | BAY-13 | 4864799 | ELSTER | Kvarh(Lead/Lag) | 200 | 999409 | 999409 | 0 | 0 | 0 | 966844 | 968432 | -1588 | -317600 | -0.3176
4 | BAY-53 | 4865127 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 999793 | 999793 | 0 | 0 | 0 | 995703 | 995744 | -41 | -54666.53 | -0.054667
5 | BAY-54 | 4865177 | ELSTER | Kvarh(Lead/Lag) | 1500 | 997346 | 997349 | -3 | -4500 | -0.0045 | 997404 | 997491 | -87 | -130500 | -0.1305
6 | BAY-7 | 4865111 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 10343 | 10343 | 0 | 0 | 0 | 18395 | 18519 | -124 | -165332.92 | -0.16533
7 | BAY-37 | 4865160 | ELSTER | Kvarh(Lead/Lag) | 1000 | 994471 | 994476 | -5 | -5000 | -0.005 | 995017 | 995153 | -136 | -136000 | -0.136
8 | BAY-9 | 4865157 | ELSTER | Kvarh(Lead/Lag) | 1000 | 990604 | 990604 | 0 | 0 | 0 | 985370 | 985503 | -133 | -133000 | -0.133
9 | BAY-5 LAJPAT NAGAR | 4865179 | ELSTER | Kvarh(Lead/Lag) | 800 | 999995 | 999995 | 0 | 0 | 0 | 998256 | 998498 | -242 | -193600 | -0.1936
10 | BAY-38 | 4865130 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 988546 | 988546 | 0 | 0 | 0 | 264990 | 265008 | -18 | -23999.94 | -0.024
PAAPANKALAN-I
11 | Tx.1 | 4864786 | ELSTER | Kvarh(Lead/Lag) | -6666.666 | 1018 | 954 | 64 | -426666.624 | -0.42667 | 106 | 106 | 0 | 0 | 0
12 | Tx.2 | 4865025 | ELSTER | Kvarh(Lead/Lag) | -1000 | 36594 | 34627 | 1967 | -1967000 | -1.967 | 997368 | 997368 | 0 | 0 | 0
13 | Tx.3 | 5128433 | ELSTER | Kvarh(Lead/Lag) | -2000 | 5597 | 5292 | 305 | -610000 | -0.61 | 999706 | 999700 | 6 | -12000 | -0.012
14 | Tx.5 | 5128464 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1882 | 1648 | 234 | -234000 | -0.234 | 996070 | 996081 | -11 | 11000 | 0.011
PAAPANKALAN-II
15 | Tx.1 | 4864958 | ELSTER | Kvarh(Lead/Lag) | -1250 | 1516 | 441 | 1075 | -1343750 | -1.3438 | 166 | 166 | 0 | 0 | 0
16 | Tx.2 | 5128438 | ELSTER | Kvarh(Lead/Lag) | -1000 | 13644 | 13444 | 200 | -200000 | -0.2 | 567 | 564 | 3 | -3000 | -0.003
17 | Tx.3 | 4864988 | ELSTER | Kvarh(Lead/Lag) | -2000 | 38629 | 38482 | 147 | -294000 | -0.294 | 5492 | 5448 | 44 | -88000 | -0.088
18 | Tx.4 | 4864938 | ELSTER | Kvarh(Lead/Lag) | -2000 | 4369 | 4165 | 204 | -408000 | -0.408 | 999822 | 999822 | 0 | 0 | 0
PAAPANKALAN-III
19 | Tx.1 | 4864912 | ELSTER | Kvarh(Lead/Lag) | -1600 | 3596 | 740 | 2856 | -4569600 | -4.5696 | 1812 | 1810 | 2 | -3200 | -0.0032
20 | Tx.2 | 5128459 | ELSTER | Kvarh(Lead/Lag) | -800 | 134378 | 130623 | 3755 | -3004000 | -3.004 | 7885 | 7882 | 3 | -2400 | -0.0024
NAJAFGARH
21 | Tx.1 | 4864867 | ELSTER | Kvarh(Lead/Lag) | -2500 | 999743 | 999641 | 102 | -255000 | -0.255 | 999900 | 999900 | 0 | 0 | 0
22 | Tx.2 | 4865036 | ELSTER | Kvarh(Lead/Lag) | -2000 | 952344 | 952205 | 139 | -278000 | -0.278 | 989296 | 989317 | -21 | 42000 | 0.042
23 | Tx.3 | 4864787 | ELSTER | Kvarh(Lead/Lag) | -2000 | 998574 | 998786 | -212 | 424000 | 0.424 | 999993 | 999993 | 0 | 0 | 0
24 | Tx.4 | 4864989 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999889 | 999256 | 633 | -633000 | -0.633 | 999935 | 999935 | 0 | 0 | 0
R.K.PURAM
25 | 33KV I/C-1 | 5295131 | ELSTER | Kvarh(Lead/Lag) | -1000 | 997584 | 997431 | 153 | -153000 | -0.153 | 997257 | 997257 | 0 | 0 | 0
26 | 33KV I/C-2 | 5295139 | ELSTER | Kvarh(Lead/Lag) | -1000 | 981464 | 981307 | 157 | -157000 | -0.157 | 12976 | 12976 | 0 | 0 | 0
27 | 66KV I/C-1 | 5295173 | ELSTER | Kvarh(Lead/Lag) | -1000 | 296163 | 294645 | 1518 | -1518000 | -1.518 | 140060 | 140060 | 0 | 0 | 0
28 | 66KV I/C-2 | 5100228 | ELSTER | Kvarh(Lead/Lag) | -2000 | 8484 | 8136 | 348 | -696000 | -0.696 | 1544 | 1544 | 0 | 0 | 0
IMPORT
MANGOLPURI
29 | NANGLOI-2 (03) IMP. | Y0357821 | Secure | Kvarh(Lead/Lag) | 0.8 | 761000 | 713000 | 48000 | 38400 | 0.0384 | 9000 | 9000 | 0 | 0 | 0
LODHI ROAD
30 | Tx.1 | 5269210 | ELSTER | Kvarh(Lead/Lag) | -1000 | 929113 | 930595 | -1482 | 1482000 | 1.482 | 965242 | 965242 | 0 | 0 | 0
31 | Tx.2 | 5269749 | ELSTER | Kvarh(Lead/Lag) | -1000 | 992042 | 991985 | 57 | -57000 | -0.057 | 999495 | 999495 | 0 | 0 | 0
32 | Tx.3 | 4864945 | ELSTER | Kvarh(Lead/Lag) | -1000 | 4747 | 2546 | 2201 | -2201000 | -2.201 | 999976 | 999976 | 0 | 0 | 0
TUGLAKABAD
33 | 66KV I/C-1 | 5128460 | ELSTER | Kvarh(Lead/Lag) | -800 | 41718 | 41467 | 251 | -200800 | -0.2008 | 15449 | 15388 | 61 | -48800 | -0.0488
34 | 66KV I/C-2 | 4902495 | ELSTER | Kvarh(Lead/Lag) | -1200 | 235 | 55 | 180 | -216000 | -0.216 | 521 | 478 | 43 | -51600 | -0.0516
OKHLA
35 | Tx.1 (66 KV)-circuit No.1 | 5128411 | ELSTER | Kvarh(Lead/Lag) | -2000 | 999823 | 999639 | 184 | -368000 | -0.368 | 1196 | 1150 | 46 | -92000 | -0.092
36 | Tx.2 (66 KV)-circuit no. 2 | 4864947 | ELSTER | Kvarh(Lead/Lag) | -1000 | 232 | 231 | 1 | -1000 | -0.001 | 1000014 | 999948 | 66 | -66000 | -0.066
37 | Tx.5 (33 KV)-Ckt No.3 | 5128413 | ELSTER | Kvarh(Lead/Lag) | -1000 | 0 | 0 | 0 | 0 | 0 | 52 | 5 | 47 | -47000 | -0.047
38 | Tx.3 (33 KV)-Ckt No.4 | 4864904 | ELSTER | Kvarh(Lead/Lag) | -1000 | 5727 | 5712 | 15 | -15000 | -0.015 | 996843 | 996817 | 26 | -26000 | -0.026
39 | Tx.4 (33 KV)-Ckt No. 5 | 4864942 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1324 | 1324 | 0 | 0 | 0 | 2183 | 1720 | 463 | -463000 | -0.463
BRPL(+) continue | [14 empty] | NOVEMBER-2023
VASANT KUNJ
40 | Tx.1 | 4864920 | ELSTER | Kvarh(Lead/Lag) | -1000 | 11297 | 8831 | 2466 | -2466000 | -2.466 | 73 | 73 | 0 | 0 | 0
41 | Tx.2 | 4865038 | ELSTER | Kvarh(Lead/Lag) | -1000 | 25169 | 25125 | 44 | -44000 | -0.044 | 928 | 920 | 8 | -8000 | -0.008
42 | Tx.3 | 5295165 | ELSTER | Kvarh(Lead/Lag) | -1000 | 41232 | 41042 | 190 | -190000 | -0.19 | 968783 | 968783 | 0 | 0 | 0
MEHRAULI
43 | Tx.1 | 4864916 | ELSTER | Kvarh(Lead/Lag) | -1000 | 930 | 567 | 363 | -363000 | -0.363 | 3 | 17 | -14 | 14000 | 0.014
44 | Tx.2 | 4864806 | ELSTER | Kvarh(Lead/Lag) | -500 | 21934 | 18628 | 3306 | -1653000 | -1.653 | 1915 | 1914 | 1 | -500 | -0.0005
45 | Tx.3 | 4864840 | ELSTER | Kvarh(Lead/Lag) | -2500 | 2953 | 2793 | 160 | -400000 | -0.4 | 1125 | 1130 | -5 | 12500 | 0.0125
46 | Tx.4 | 4865042 | ELSTER | Kvarh(Lead/Lag) | -2000 | 5989 | 5090 | 899 | -1798000 | -1.798 | 1085 | 1084 | 1 | -2000 | -0.002
RIDGE VALLEY
47 | Tx-1 | 5128461 | ELSTER | Kvarh(Lead/Lag) | -1000 | 103260 | 100522 | 2738 | -2738000 | -2.738 | 996803 | 996803 | 0 | 0 | 0
48 | Tx-2 | 4865003 | ELSTER | Kvarh(Lead/Lag) | -2000 | 73466 | 71721 | 1745 | -3490000 | -3.49 | 999341 | 999341 | 0 | 0 | 0
DIAL
49 | Tx-1 | 5128472 | ELSTER | Kvarh(Lead/Lag) | -1500 | 13191 | 11525 | 1666 | -2499000 | -2.499 | 57 | 57 | 0 | 0 | 0
50 | Tx-2 | 5128452 | ELSTER | Kvarh(Lead/Lag) | -1000 | 15725 | 15301 | 424 | -424000 | -0.424 | 999997 | 999997 | 0 | 0 | 0
MASJID MOD
51 | Tx-1 | 4864905 | ELSTER | Kvarh(Lead/Lag) | -1000 | 996745 | 996780 | -35 | 35000 | 0.035 | 144 | 152 | -8 | 8000 | 0.008
52 | Tx-2 | 4902504 | ELSTER | Kvarh(Lead/Lag) | -1000 | 991203 | 991269 | -66 | 66000 | 0.066 | 994719 | 994735 | -16 | 16000 | 0.016
53 | Tx-3 | 5128426 | ELSTER | Kvarh(Lead/Lag) | -1000 | 989849 | 989603 | 246 | -246000 | -0.246 | 986715 | 986717 | -2 | 2000 | 0.002
MUNDKA
54 | 66KV NANGLOI | 4902509 | ELSTER | Kvarh(Lead/Lag) | 4000 | 993286 | 993521 | -235 | -940000 | -0.94 | 999990 | 999990 | 0 | 0 | 0
55 | 66KV NGL. WATER WORKS | 4865026 | ELSTER | Kvarh(Lead/Lag) | 800 | 960547 | 961293 | -746 | -596800 | -0.5968 | 626 | 626 | 0 | 0 | 0
56 | 66KV DMRC | 5100233 | ELSTER | Kvarh(Lead/Lag) | 800 | 905311 | 905706 | -395 | -316000 | -0.316 | 999425 | 999425 | 0 | 0 | 0
57 | 66KV NGL. T-OFF MGL P | 4864971 | ELSTER | Kvarh(Lead/Lag) | -800 | 0 | 0 | 0 | 0 | 0 | 999495 | 999495 | 0 | 0 | 0
58 | BAY No 611 | 4864985 | ELSTER | Kvarh(Lead/Lag) | 800 | 63 | 206 | -143 | -114400 | -0.1144 | 4 | 4 | 0 | 0 | 0
59 | BAY No 612 | 5128436 | ELSTER | Kvarh(Lead/Lag) | 800 | 992557 | 992677 | -120 | -96000 | -0.096 | 58 | 58 | 0 | 0 | 0 | Data upto 19-11-2023
[10 empty] | -0.064 |  |  |  |  | 0 | Assessment(19.11.23 To 01.12.23)
60 | 66KV Nilothi Ckt-1 | 5128428 | ELSTER | Kvarh(Lead/Lag) | 800 | 983079 | 983800 | -721 | -576800 | -0.5768 | 999382 | 999383 | -1 | -800 | -0.0008
61 | 66KV Nilothi Ckt-2 | 4864926 | ELSTER | Kvarh(Lead/Lag) | 800 | 979396 | 981257 | -1861 | -1488800 | -1.4888 | 999967 | 999967 | 0 | 0 | 0
PARK STREET
63 | 66KV R VALLEY-1 | Y0357818 | Secure | Kvarh(Lead/Lag) | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SARITA VIHAR
64 | TX-1 | 4864966 | ELSTER | Kvarh(Lead/Lag) | -2000 | 131679 | 130952 | 727 | -1454000 | -1.454 | 7527 | 7527 | 0 | 0 | 0 | Data upto 06.11.2023
|  | 4864979 | ELSTER | Kvarh(Lead/Lag) | -2000 | 43635 | 39733 | 3902 | -7804000 | -7.804 | 8396 | 8396 | 0 | 0 | 0 | Check Data (06.11.23 To 01.12.23)
64 | Tx-2 | 4864932 | ELSTER | Kvarh(Lead/Lag) | -1000 | 19678 | 19648 | 30 | -30000 | -0.03 | 17285 | 16897 | 388 | -388000 | -0.388
65 | Tx-3 | 4864999 | ELSTER | Kvarh(Lead/Lag) | -1000 | 144586 | 143559 | 1027 | -1027000 | -1.027 | 3506 | 3506 | 0 | 0 | 0
NARAINA
66 | GOPI NATH BAZAAR | 4902566 | ELSTER | Kvarh(Lead/Lag) | 100 | 679 | 680 | -1 | -100 | -0.0001 | 3666 | 3573 | 93 | 9300 | 0.0093
SUDARSHAN PARK
67 | VISHAL | 4865149 | ELSTER | Kvarh(Lead/Lag) | 187.5 | 995887 | 996030 | -143 | -26812.5 | -0.026812 | 998246 | 998248 | -2 | -375 | -0.000375
68 | MAYA PURI -I | 4864870 | ELSTER | Kvarh(Lead/Lag) | 1000 | 998039 | 998128 | -89 | -89000 | -0.089 | 428 | 423 | 5 | 5000 | 0.005
69 | MAYA PURI -II | 5128400 | ELSTER | Kvarh(Lead/Lag) | 1000 | 997439 | 997582 | -143 | -143000 | -0.143 | 400 | 399 | 1 | 1000 | 0.001
KANJAWALA
70 | 66KV DMRC | Y0357713 | Secure | Kvarh(Lead/Lag) | 0.4 | -1067000 | -1052000 | -15000 | -6000 | -0.006 | -680000 | -37000 | -643000 | -257200 | -0.2572
Trauma Centre
71 | 33kV Bhikaji Cama Place | 4864839 | ELSTER | Kvarh(Lead/Lag) | 1000 | 758 | 950 | -192 | -192000 | -0.192 | 999777 | 999777 | 0 | 0 | 0
72 | IIT CIRCUIT | 4864872 | ELSTER | Kvarh(Lead/Lag) | 1000 | 996074 | 996765 | -691 | -691000 | -0.691 | 999564 | 999564 | 0 | 0 | 0
A.I.I.M.S.
73 | 11KV VIKAS SADAN | 4865072 | ELSTER | Kvarh(Lead/Lag) | 100 | 999830 | 999916 | -86 | -8600 | -0.0086 | 999678 | 999678 | 0 | 0 | 0
74 | 11KV NDSE | 4865066 | ELSTER | Kvarh(Lead/Lag) | 200 | 237 | 159 | 78 | 15600 | 0.0156 | 407 | 407 | 0 | 0 | 0
PEERGARHI
75 | 33KV VISHAL (L-3) | 4864861 | ELSTER | Kvarh(Lead/Lag) | 500 | 8069 | 8137 | -68 | -34000 | -0.034 | 3021 | 3019 | 2 | 1000 | 0.001
76 | 33KV (LINE - 4) | 4864877 | ELSTER | Kvarh(Lead/Lag) | 1000 | 994008 | 994046 | -38 | -38000 | -0.038 | 4158 | 4162 | -4 | -4000 | -0.004
77 | 33KV UDYOG NAGAR(L-5) | 4864841 | ELSTER | Kvarh(Lead/Lag) | 1000 | 980398 | 980421 | -23 | -23000 | -0.023 | 526 | 521 | 5 | 5000 | 0.005
78 | 33KV MADIPUR(L-6) | 4864882 | ELSTER | Kvarh(Lead/Lag) | 1000 | 7540 | 7547 | -7 | -7000 | -0.007 | 6948 | 6948 | 0 | 0 | 0
79 | PASCHIM PURI - I (L-7) | 4865064 | ELSTER | Kvarh(Lead/Lag) | 150 | 993315 | 993389 | -74 | -11100 | -0.0111 | 433 | 427 | 6 | 900 | 0.0009
80 | PASCHIM PURI - 2(L-8) | 4864948 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999964 | 999977 | -13 | -13000 | -0.013 | 2 | 1 | 1 | 1000 | 0.001
81 | MUKHERJEE PARK - I | 4864790 | ELSTER | Kvarh(Lead/Lag) | 266.67 | 3294 | 3267 | 27 | 7200.09 | 0.0072001 | 670 | 665 | 5 | 1333.35 | 0.0013334
82 | MUKHERJEE PARK - II | 4865154 | ELSTER | Kvarh(Lead/Lag) | 1000 | 0 | 25 | -25 | -25000 | -0.025 | 11 | 3 | 8 | 8000 | 0.008
REWARI LINE
83 | VISHAL-1 | [8 empty] | -0.0374 |  |  |  |  | 0 | Assessment(01.11.23 To 09.11.23)
|  | 4902510 | ELSTER | Kvarh(Lead/Lag) | 400 | 999743 | 1000000 | -257 | -102800 | -0.1028 | 0 | 0 | 0 | 0 | 0 | w.e.f 09-11-2023
84 | VISHAL-2 | 4865140 | ELSTER | Kvarh(Lead/Lag) | 937.5 | 999825 | 999963 | -138 | -129375 | -0.12937 | 999739 | 999740 | -1 | -937.5 | -0.0009375
85 | MAYAPURI | 4864808 | ELSTER | Kvarh(Lead/Lag) | 187.5 | 980278 | 980806 | -528 | -99000 | -0.099 | 2532 | 2533 | -1 | -187.5 | -0.0001875
86 | 20MVATX-III | 4865080 | ELSTER | Kvarh(Lead/Lag) | 2500 | 999982 | 999999 | -17 | -42500 | -0.0425 | 999997 | 999997 | 0 | 0 | 0
87 | 16MVA TX-1 | 4864822 | ELSTER | Kvarh(Lead/Lag) | 100 | 993010 | 993052 | -42 | -4200 | -0.0042 | 32214 | 32214 | 0 | 0 | 0
SUM OF ENERGY RELEASED AT 66/33/11 KV LEVEL | [9 empty] | -50.2888 |  |  |  |  | -3.0837
BRPL (-) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 % |  |  | NOVEMBER-2023
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
TILAK MARG
1 | EXHB-II | 4865151 | ELSTER | Kvarh(Lead/Lag) | -500 | 21875 | 21883 | -8 | 4000 | 0.004 | 6207 | 6211 | -4 | 2000 | 0.002
EXPORT TO EAST & CENTRE
RIDGE VALLEY
2 | O/G SHANKAR RD.1 | 4865137 | ELSTER | Kvarh(Lead/Lag) | -1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | O/G SHANKAR RD.2 | 4864828 | ELSTER | Kvarh(Lead/Lag) | -133.33 | 992395 | 992409 | -14 | 1866.62 | 0.0018666 | 1886 | 2012 | -126 | 16799.58 | 0.0168
4 | KHYBER LANE-1 EXP. | 4865164 | ELSTER | Kvarh(Lead/Lag) | -666.667 | 999667 | 999795 | -128 | 85333.376 | 0.085333 | 519 | 557 | -38 | 25333.346 | 0.025333
5 | KHYBER LANE-2 EXP. | 4864845 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1064 | 1105 | -41 | 41000 | 0.041 | 369 | 366 | 3 | -3000 | -0.003
6 | 33KV R R HOSPITAL | Q0819156 | SECURE | Kvarh(Lead/Lag) | -2 | 0 | 0 | 0 | 0 | 0 | 30500 | -800 | 31300 | -62600 | -0.0626 | w.e.f 19-10-2023
EXPORTS(*)
EXPORT TO NDMC
7 | SPM NO.1/ BAPUDHAM | 4864955 | ELSTER | Kvarh(Lead/Lag) | -1000 | 988757 | 989277 | -520 | 520000 | 0.52 | 2698 | 2698 | 0 | 0 | 0
8 | SPM NO.2 | 4864820 | ELSTER | Kvarh(Lead/Lag) | -160 | 2683 | 2829 | -146 | 23360 | 0.02336 | 45949 | 45980 | -31 | 4960 | 0.00496
9 | NEHRU PARK | 4864811 | ELSTER | Kvarh(Lead/Lag) | -200 | 3832 | 3859 | -27 | 5400 | 0.0054 | 27028 | 27041 | -13 | 2600 | 0.0026
10 | Guest House | 4864961 | ELSTER | Kvarh(Lead/Lag) | -1000 | 967174 | 967906 | -732 | 732000 | 0.732 | 999625 | 999625 | 0 | 0 | 0
EXPORT TO NDMC
11 | SHAN NAGAR 1 | 4902580 | ELSTER | Kvarh(Lead/Lag) | -100 | 923 | 903 | 20 | -2000 | -0.002 | 3610 | 3604 | 6 | -600 | -0.0006
12 | SHAN NAGAR 2 | 4902544 | ELSTER | Kvarh(Lead/Lag) | -100 | 5830 | 5686 | 144 | -14400 | -0.0144 | 5938 | 5935 | 3 | -300 | -0.0003
13 | 33KV SAHJAHAN ROAD | 4864793 | ELSTER | Kvarh(Lead/Lag) | -200 | 999457 | 999926 | -469 | 93800 | 0.0938 | 999703 | 999703 | 0 | 0 | 0
EXPORTS(*)
A.I.I.M.S.
14 | KILOKARI | 4865103 | ELSTER | Kvarh(Lead/Lag) | 833.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | SIRI FORT | 4865114 | ELSTER | Kvarh(Lead/Lag) | 833.33 | 0 | 0 | 0 | 0 | 0 | 999871 | 999871 | 0 | 0 | 0
16 | RIDGE VALLEY | 4902508 | ELSTER | Kvarh(Lead/Lag) | 833.33 | 359 | 241 | 118 | 98332.94 | 0.098333 | 7131 | 7032 | 99 | 82499.67 | 0.0825
KIDWAI NAGAR
17 | I/C from R.Valley at kidwai ngr | 4864850 | ELSTER | Kvarh(Lead/Lag) | -625 | 472 | 455 | 17 | -10625 | -0.010625 | 8186 | 8083 | 103 | -64375 | -0.064375
EXCHANGE OF ENERGY 11KV
EXPORTS
VISHAL
18 | RAMESH NAGAR-1 | 4865065 | ELSTER | Kvarh(Lead/Lag) | -266.667 | 0 | 0 | 0 | 0 | 0 | 999995 | 999995 | 0 | 0 | 0
19 | BALI NAGAR -1 | 4902541 | ELSTER | Kvarh(Lead/Lag) | -100 | 999482 | 999482 | 0 | 0 | 0 | 999486 | 999486 | 0 | 0 | 0
20 | ESI HOSPITAL | 4902539 | ELSTER | Kvarh(Lead/Lag) | -100 | 3156 | 3231 | -75 | 7500 | 0.0075 | 35655 | 35650 | 5 | -500 | -0.0005
S.B.MILL
21 | MOTI NAGAR KIOSK | 4902591 | ELSTER | Kvarh(Lead/Lag) | -1333 | 746 | 746 | 0 | 0 | 0 | 634 | 641 | -7 | 9331 | 0.009331
22 | 53 RAMA ROAD | 4902528 | ELSTER | Kvarh(Lead/Lag) | -100 | 298 | 298 | 0 | 0 | 0 | 4664 | 4664 | 0 | 0 | 0
23 | BREAK FAST | 4902523 | ELSTER | Kvarh(Lead/Lag) | -100 | 999815 | 999815 | 0 | 0 | 0 | 999943 | 999943 | 0 | 0 | 0
24 | 70 RAMA ROAD | 4865093 | ELSTER | Kvarh(Lead/Lag) | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | MOTI NAGAR 2 | 4902548 | ELSTER | Kvarh(Lead/Lag) | -100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | NAJAFGARH ROAD | 4902564 | ELSTER | Kvarh(Lead/Lag) | -100 | 1616 | 1616 | 0 | 0 | 0 | 12625 | 12291 | 334 | -33400 | -0.0334
REWARI LINE (11KV TRANSFER OF ENERGY)
27 | BSES -NDPL(EX.) ON BUS-1&2 | 4902529 | ELSTER | Kvarh(Lead/Lag) | 400 | 999999 | 999999 | 0 | 0 | 0 | 999999 | 999999 | 0 | 0 | 0
28 | BSES -NDPL(EX.) ON BUS-2&3 | 4902525 | ELSTER | Kvarh(Lead/Lag) | -400 | 999895 | 999895 | 0 | 0 | 0 | 999460 | 999460 | 0 | 0 | 0
RIDGE VALLEY (RAILWAY CKTS)
29 | 66KV RLY Ckt-1 | 4864994 | ELSTER | Kvarh(Lead/Lag) | -800 | 2437 | 1898 | 539 | -431200 | -0.4312 | 1593 | 1593 | 0 | 0 | 0
REWARI LINE
30 | PPK-1 | 4864960 | ELSTER | Kvarh(Lead/Lag) | -1000 | 978018 | 979079 | -1061 | 1061000 | 1.061 | 1762 | 1762 | 0 | 0 | 0
31 | SAGARPUR | 5129960 | ELSTER | Kvarh(Lead/Lag) | -281.25 | 999557 | 999566 | -9 | 2531.25 | 0.0025313 | 430 | 430 | 0 | 0 | 0
FED FROM BRPL(RLY.)
32 | NIZAMUDDIN RLY STN | Q0430831 | SECURE | Kvarh(Lead/Lag) | -600 | 0.12 | 0.12 | 0 | 0 | 0 | 48.08 | 45.88 | 2.2 | -1320 | -0.00132
33 | TUGLUKABAD RY STN | Q0430821 | SECURE | Kvarh(Lead/Lag) | -3000 | 0.49 | 0.34 | 0.15 | -450 | -0.00045 | 27.09 | 25.3 | 1.79 | -5370 | -0.00537
TOTAL OF ENERGY AT INTER COMPANY EXCHANGE POINTS | [9 empty] | 2.2174 |  |  |  |  | -0.027941
NOVEMBER-2023
EXECUTIVE SUMMERY BSES R.P. LTD.
1) ENERGY RELEASED AT 66/33/11 KV LEVEL (REFER SHEET BRPL (+)) | [9 empty] | -50.2888 |  |  |  |  | -3.0837
2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer sheet BRPL(-)) | [9 empty] | 2.2174 |  |  |  |  | -0.027941
3)ENERGY RECEIVED FROM ROHTAK ROAD (REFER ROHTAK ROAD SHEET ENC.) | [9 empty] | -0.55067 |  |  |  |  | 0.0005
4) ENERGY RELEASED TO MES BY BRPL | [9 empty] | -0.02005 |  |  |  |  | -0.049925
NET ENERGY TO BSES RAJDHANI POWER LIMITED | [9 empty] | -48.6421 |  |  |  |  | -3.161
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | -48.6421 | (REACTIVE MUs) |  |  |  | -3.161 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | 9.9046 | (REACTIVE MUs) |  |  |  | 0.020404 | (REACTIVE MUs)
[9 empty] | TOTAL | -38.7375 | (REACTIVE MUs) |  |  |  | -3.1406 | (REACTIVE MUs)

## BYPL
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [15 empty] | NOVEMBER-2023
Customer:BSES YAMUNA POWER LIMITED.
BYPL(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
I.P.STATION 33KV FEEDER
1 | KAMLA MKT.-B-18 | 4865110 | ELSTER | Kvarh(Lead/Lag) | 267 | 36461 | 36461 | 0 | 0 | 0 | 978090 | 978241 | -151 | -40317 | -0.040317
2 | KAMLA MKT.B-30 | 4865180 | ELSTER | Kvarh(Lead/Lag) | 4000 | 0 | 0 | 0 | 0 | 0 | 999020 | 999066 | -46 | -184000 | -0.184
3 | P. HOSPITAL BAY-19 | 4865108 | ELSTER | Kvarh(Lead/Lag) | 133.33 | 24928 | 24928 | 0 | 0 | 0 | 33709 | 33736 | -27 | -3599.91 | -0.0035999
4 | IG STD- BAY-29 | 4864834 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999585 | 999586 | -1 | -1000 | -0.001 | 998565 | 998588 | -23 | -23000 | -0.023
5 | IG STD-BAY 31 | 4865126 | ELSTER | Kvarh(Lead/Lag) | 1600 | 88 | 88 | 0 | 0 | 0 | 999212 | 999261 | -49 | -78400 | -0.0784
6 | DELHI GATE B-17 | 4865104 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 18403 | 18403 | 0 | 0 | 0 | 3251 | 3219 | 32 | 42666.56 | 0.042667
7 | MINTO RD. B-34 | 4864795 | ELSTER | Kvarh(Lead/Lag) | 200 | 999518 | 999521 | -3 | -600 | -0.0006 | 989518 | 990845 | -1327 | -265400 | -0.2654
RPH
8 | KAMLA MKT.-2 | 4865183 | ELSTER | Kvarh(Lead/Lag) | 4000 | 999808 | 999906 | -98 | -392000 | -0.392 | 999976 | 999976 | 0 | 0 | 0
9 | FOUNTAIN BAY-16 | 4864897 | ELSTER | Kvarh(Lead/Lag) | 500 | 982550 | 982733 | -183 | -91500 | -0.0915 | 555 | 555 | 0 | 0 | 0
10 | MINTO RD BAY-17 | 4864849 | ELSTER | Kvarh(Lead/Lag) | 1000 | 997125 | 997184 | -59 | -59000 | -0.059 | 999767 | 999767 | 0 | 0 | 0
11 | TOWN HALL-3 | 4864833 | ELSTER | Kvarh(Lead/Lag) | 1000 | 982396 | 982457 | -61 | -61000 | -0.061 | 1004 | 1004 | 0 | 0 | 0
12 | LAHORI GATE-1 | 4865120 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 999963 | 999965 | -2 | -2666.66 | -0.0026667 | 3390 | 3375 | 15 | 19999.95 | 0.02
13 | LAHORI GATE-2 | 4864889 | ELSTER | Kvarh(Lead/Lag) | 1000 | 993322 | 993352 | -30 | -30000 | -0.03 | 994553 | 994554 | -1 | -1000 | -0.001
14 | JAMA MASJID-1 | 4864859 | ELSTER | Kvarh(Lead/Lag) | 1000 | 992494 | 992495 | -1 | -1000 | -0.001 | 999769 | 999788 | -19 | -19000 | -0.019
15 | JAMA MASJID-2 | 4864895 | ELSTER | Kvarh(Lead/Lag) | 800 | 994328 | 994334 | -6 | -4800 | -0.0048 | 6757 | 6763 | -6 | -4800 | -0.0048
16 | GB PANTH(Bay-13) | 4864826 | ELSTER | Kvarh(Lead/Lag) | 133.33 | 14949 | 14961 | -12 | -1599.96 | -0.0016 | 8690 | 8690 | 0 | 0 | 0
17 | SACHV. (Bay-12) | 4865143 | ELSTER | Kvarh(Lead/Lag) | 1000 | 25 | 29 | -4 | -4000 | -0.004 | 999858 | 999864 | -6 | -6000 | -0.006
18 | KAMLA MKT. (B-19) | 4864883 | ELSTER | Kvarh(Lead/Lag) | 1000 | 372 | 400 | -28 | -28000 | -0.028 | 16397 | 16397 | 0 | 0 | 0
GT
19 | DMRC. CKT.-I | 4864954 | ELSTER | Kvarh(Lead/Lag) | 1250 | 940361 | 942402 | -2041 | -2551250 | -2.5513 | 947108 | 947108 | 0 | 0 | 0
20 | DMRC CKT.-II | 4865030 | ELSTER | Kvarh(Lead/Lag) | 1000 | 917235 | 920742 | -3507 | -3507000 | -3.507 | 933434 | 933434 | 0 | 0 | 0
21 | AKSHARDHAM | 4865027 | ELSTER | Kvarh(Lead/Lag) | 1000 | 999431 | 999431 | 0 | 0 | 0 | 999959 | 999959 | 0 | 0 | 0
| KASHMIRI GATE | [8 empty] | -6.0583 |  |  |  |  | 0
22 | 100 MVA TX.-1 | 4902505 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999993 | 999994 | -1 | 1000 | 0.001 | 999725 | 999788 | -63 | 63000 | 0.063
23 | 100 MVA TX.-2 | 5295140 | ELSTER | Kvarh(Lead/Lag) | -1000 | 6635 | 6612 | 23 | -23000 | -0.023 | 985192 | 985192 | 0 | 0 | 0
24 | B/C (IMP. TO BYPL) | 4902585 | ELSTER | Kvarh(Lead/Lag) | 400 | 999998 | 999998 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0
NARAINA
25 | DMS | 4864854 | ELSTER | Kvarh(Lead/Lag) | 1000 | 998888 | 998889 | -1 | -1000 | -0.001 | 11575 | 11650 | -75 | -75000 | -0.075
PARK STREET
26 | TX.-1 (66KV) | 4864970 | ELSTER | Kvarh(Lead/Lag) | -1000 | 9542 | 6039 | 3503 | -3503000 | -3.503 | 2134 | 2130 | 4 | -4000 | -0.004
27 | TX.-2(66KV) | Y0357712 | Secure | Kvarh(Lead/Lag) | -0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | TX.-1(33KV) | 4864934 | ELSTER | Kvarh(Lead/Lag) | -1000 | 13826 | 12439 | 1387 | -1387000 | -1.387 | 999154 | 999154 | 0 | 0 | 0
29 | TX.-2(33KV) | 4864906 | ELSTER | Kvarh(Lead/Lag) | -1000 | 7631 | 7301 | 330 | -330000 | -0.33 | 998020 | 998020 | 0 | 0 | 0
HARSH VIHAR
30 | TX.-1 (66KV) | 5295177 | ELSTER | Kvarh(Lead/Lag) | -1000 | 125337 | 125292 | 45 | -45000 | -0.045 | 11871 | 11869 | 2 | -2000 | -0.002 | Data upto 08.11.23
|  | 4864933 | ELSTER | Kvarh(Lead/Lag) | -2000 | 67 | 0 | 67 | -134000 | -0.134 | 6 | 0 | 6 | -12000 | -0.012 | w.e.f 08-11-2023
31 | TX.-2 (66KV) | 5128456 | ELSTER | Kvarh(Lead/Lag) | -1000 | 97725 | 97269 | 456 | -456000 | -0.456 | 6269 | 6263 | 6 | -6000 | -0.006
32 | TX.-3 (66KV) | 4864830 | ELSTER | Kvarh(Lead/Lag) | -5000 | 3432 | 3173 | 259 | -1295000 | -1.295 | 439 | 439 | 0 | 0 | 0
IMPORTS
SUBZI MANDI
33 | O/G BG Rd.1 | 4864899 | ELSTER | Kvarh(Lead/Lag) | 500 | 973179 | 973189 | -10 | -5000 | -0.005 | 992117 | 992116 | 1 | 500 | 0.0005
34 | O/G BG Rd.2 | 4864825 | ELSTER | Kvarh(Lead/Lag) | 133.33 | 7747 | 7978 | -231 | -30799.23 | -0.030799 | 8370 | 8370 | 0 | 0 | 0
RIDGE VALLEY
35 | O/G SHANKAR RD.1 | 4865137 | ELSTER | Kvarh(Lead/Lag) | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | O/G SHANKAR RD.2 | 4864828 | ELSTER | Kvarh(Lead/Lag) | 133 | 992395 | 992409 | -14 | -1862 | -0.001862 | 1886 | 2012 | -126 | -16758 | -0.016758
PREET VIHAR
37 | TX-1 | 5295145 | ELSTER | Kvarh(Lead/Lag) | -1000 | 976796 | 976221 | 575 | -575000 | -0.575 | 990269 | 990269 | 0 | 0 | 0
[5 empty] | -1000 | 995917 | 995900 | 17 | -17000 | -0.017
38 | Tx-2 | 5295146 | ELSTER | Kvarh(Lead/Lag) | -1000 | 963531 | 963032 | 499 | -499000 | -0.499 | 969522 | 969523 | -1 | 1000 | 0.001
[5 empty] | -1000 | 978952 | 978751 | 201 | -201000 | -0.201
DEV NAGAR
39 | TX.-3 (33KV) | Q0487636 | Secure | Kvarh(Lead/Lag) | -1 | -191000 | -851000 | 660000 | -660000 | -0.66 | 0 | 0 | 0 | 0 | 0
40 | TX.-4 (33KV) | Q0487633 | Secure | Kvarh(Lead/Lag) | -1 | 1744000 | 900000 | 844000 | -844000 | -0.844 | 0 | 0 | 0 | 0 | 0
| ENERGY INPUT AT 66/33KK LEVEL | [8 empty] | -16.7421 |  |  |  |  | -0.61411
| (A) NET ENERGY TO CENTRAL | [8 empty] | -16.7421 |  |  |  |  | -0.61411
NOVEMBER-2023
BYPL(+) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
S.O.W.
1 | Tx.1 | 4864977 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1297 | 743 | 554 | -554000 | -0.554 | 375 | 375 | 0 | 0 | 0
2 | Tx.2 | 4864939 | ELSTER | Kvarh(Lead/Lag) | -1000 | 820 | 32 | 788 | -788000 | -0.788 | 0 | 0 | 0 | 0 | 0
3 | Tx.3 | 5100230 | ELSTER | Kvarh(Lead/Lag) | -1000 | 477 | 247 | 230 | -230000 | -0.23 | 59 | 59 | 0 | 0 | 0
4 | Tx.4 | 4864812 | ELSTER | Kvarh(Lead/Lag) | -1000 | 2471 | 2127 | 344 | -344000 | -0.344 | 999755 | 999755 | 0 | 0 | 0
PPG
5 | Tx.1 (66 KV) | 4864978 | ELSTER | Kvarh(Lead/Lag) | -1000 | 41898 | 41851 | 47 | -47000 | -0.047 | 999037 | 998909 | 128 | -128000 | -0.128
6 | Tx.2 (66 KV) | 5128466 | ELSTER | Kvarh(Lead/Lag) | -500 | 25108 | 25008 | 100 | -50000 | -0.05 | 1632 | 1557 | 75 | -37500 | -0.0375
7 | 100 MVA Tx.1 (33 KV) | 4864973 | ELSTER | Kvarh(Lead/Lag) | -1000 | 448 | 433 | 15 | -15000 | -0.015 | 64 | 50 | 14 | -14000 | -0.014
8 | 100MVA Tx.3 (33 KV) | 5128414 | ELSTER | Kvarh(Lead/Lag) | -1000 | 63 | 22 | 41 | -41000 | -0.041 | 8 | 1 | 7 | -7000 | -0.007
9 | 100MVA Tx.4 (33 KV) | 4865024 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1980 | 1948 | 32 | -32000 | -0.032 | 110 | 101 | 9 | -9000 | -0.009
GEETA COLONY
10 | I/C-I | 5128441 | ELSTER | Kvarh(Lead/Lag) | -1000 | 154 | 57 | 97 | -97000 | -0.097 | 873 | 869 | 4 | -4000 | -0.004
11 | I/C-II | 5128429 | ELSTER | Kvarh(Lead/Lag) | -1000 | 1241 | 1157 | 84 | -84000 | -0.084 | 1669 | 1657 | 12 | -12000 | -0.012
GAZIPUR
12 | TX.-1 | 4864838 | ELSTER | Kvarh(Lead/Lag) | -5000 | 14277 | 14124 | 153 | -765000 | -0.765 | 819 | 818 | 1 | -5000 | -0.005
13 | TX-2 | 4864910 | ELSTER | Kvarh(Lead/Lag) | -1000 | 2201 | 465 | 1736 | -1736000 | -1.736 | 0 | 0 | 0 | 0 | 0
14 | TX-3 | 4864931 | ELSTER | Kvarh(Lead/Lag) | -1000 | 12526 | 11577 | 949 | -949000 | -0.949 | 912 | 912 | 0 | 0 | 0
| ENERGY INPUT AT 66/33/11KV LEVEL | [8 empty] | -5.732 |  |  |  |  | -0.2165
| (B) NET ENERGY TO EAST | [8 empty] | -5.732 |  |  |  |  | -0.2165
NOVEMBER-2023
BYPL(-) | [7 empty] | DELIEVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
KASHMIRI GATE
1 | CIVIL LINE | 4864791 | ELSTER | Kvarh(Lead/Lag) | -266.67 | 990628 | 990655 | -27 | 7200.09 | 0.0072001 | 999964 | 999962 | 2 | -533.34 | -0.00053334
2 | CIVIL LINE-2 | 4865184 | ELSTER | Kvarh(Lead/Lag) | -2000 | 6 | 6 | 0 | 0 | 0 | 80 | 70 | 10 | -20000 | -0.02
EXPORT TO NDMC FROM PARK STREET
3 | BAIRD RD.1 | 4865107 | ELSTER | Kvarh(Lead/Lag) | -266.66 | 443 | 609 | -166 | 44265.56 | 0.044266 | 2146 | 2146 | 0 | 0 | 0
4 | BAIRD RD.2 | 4865150 | ELSTER | Kvarh(Lead/Lag) | -100 | 11937 | 11115 | 822 | -82200 | -0.0822 | 1603 | 1603 | 0 | 0 | 0
5 | NIRMAN BHAWAN | 4865136 | ELSTER | Kvarh(Lead/Lag) | -200 | 970608 | 971977 | -1369 | 273800 | 0.2738 | 244 | 244 | 0 | 0 | 0
6 | H.LANE | 4865172 | ELSTER | Kvarh(Lead/Lag) | -1000 | 568 | 701 | -133 | 133000 | 0.133 | 365 | 365 | 0 | 0 | 0
7 | 66 KV BD MARG-I | 4865010 | ELSTER | Kvarh(Lead/Lag) | -800 | 999972 | 1000008 | -36 | 28800 | 0.0288 | 1116 | 1115 | 1 | -800 | -0.0008
8 | 66 KV BD MARG-II | 4865004 | ELSTER | Kvarh(Lead/Lag) | -800 | 1594 | 1764 | -170 | 136000 | 0.136 | 2264 | 2265 | -1 | 800 | 0.0008
9 | 66KV DMRC-I | 4865050 | ELSTER | Kvarh(Lead/Lag) | -800 | 982119 | 982119 | 0 | 0 | 0 | 998603 | 998603 | 0 | 0 | 0
10 | 66KV DMRC-II | 4864998 | ELSTER | Kvarh(Lead/Lag) | -800 | 950267 | 950267 | 0 | 0 | 0 | 979419 | 979419 | 0 | 0 | 0
11 | 66KV GUEST HOUSE | 4864993 | ELSTER | Kvarh(Lead/Lag) | -800 | 940026 | 941412 | -1386 | 1108800 | 1.1088 | 987524 | 987526 | -2 | 1600 | 0.0016
12 | 66KV SCHOOL LANE | 5128403 | ELSTER | Kvarh(Lead/Lag) | -2000 | 992281 | 992327 | -46 | 92000 | 0.092 | 998064 | 998074 | -10 | 20000 | 0.02
EXPORT TO SOUTH & WEST FROM PARK STREET
13 | 66KV R VALLEY-1 | Y0357818 | SECURE | Kvarh(Lead/Lag) | -0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EXPORT TO NORTH from SHASTRI PARK
14 | PUSA GRID-I | 4864843 | ELSTER | Kvarh(Lead/Lag) | -1000 | 993009 | 993365 | -356 | 356000 | 0.356 | 24322 | 24322 | 0 | 0 | 0
DMS
15 | 33KV PANDAV NGR | 4902578 | ELSTER | Kvarh(Lead/Lag) | -300 | 998507 | 998507 | 0 | 0 | 0 | 999767 | 999767 | 0 | 0 | 0
EXCHANGE OF ENERGY 11KV
EXPORTS
B.G.ROAD
16 | CSA | 4902519 | ELSTER | Kvarh(Lead/Lag) | -500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | DCM NO.1 | 4902579 | ELSTER | Kvarh(Lead/Lag) | -500 | 999859 | 999859 | 0 | 0 | 0 | 2500 | 2479 | 21 | -10500 | -0.0105
18 | DCM NO.2 | 4865089 | ELSTER | Kvarh(Lead/Lag) | -500 | 999982 | 999982 | 0 | 0 | 0 | 7 | 30 | -23 | 11500 | 0.0115
19 | SADAR S/S | 4865090 | ELSTER | Kvarh(Lead/Lag) | -500 | 1202 | 1202 | 0 | 0 | 0 | 1703 | 1674 | 29 | -14500 | -0.0145
KASHMIRI GATE
20 | 20MVA TX. | 4864797 | ELSTER | Kvarh(Lead/Lag) | -100 | 60625 | 60902 | -277 | 27700 | 0.0277 | 2652 | 2652 | 0 | 0 | 0
21 | FLY OVER | 4865074 | ELSTER | Kvarh(Lead/Lag) | -133.33 | 432 | 432 | 0 | 0 | 0 | 1215 | 1215 | 0 | 0 | 0
D.M.S
22 | PHILIPS | 4902568 | ELSTER | Kvarh(Lead/Lag) | -100 | 992598 | 992656 | -58 | 5800 | 0.0058 | 3862 | 3760 | 102 | -10200 | -0.0102
FAIZ ROAD
23 | TIBIA COLLEGE-1 | 4902599 | ELSTER | Kvarh(Lead/Lag) | -1333.33 | 33 | 32 | 1 | -1333.33 | -0.0013333 | 86 | 79 | 7 | -9333.31 | -0.0093333
24 | TIBIA COLLEGE-2 | 4902520 | ELSTER | Kvarh(Lead/Lag) | -100 | 20132 | 20096 | 36 | -3600 | -0.0036 | 6672 | 6668 | 4 | -400 | -0.0004 | Data upto 06.11.23
[10 empty] | -0.0044 |  |  |  |  | -0.0004 | Assessment(06.11.23 To 21.11.23)
|  | 4865082 | ELSTER | Kvarh(Lead/Lag) | -133.33 | 6 | 0 | 6 | -799.98 | -0.00079998 | 0 | 0 | 0 | 0 | 0 | w.e.f 21-11-2023
25 | MANAK PURA | 4902577 | ELSTER | Kvarh(Lead/Lag) | -100 | 2735 | 2605 | 130 | -13000 | -0.013 | 238 | 230 | 8 | -800 | -0.0008
FED FROM BYPL (RLY.)
26 | SADAR | Q0263400 | SECURE | Kvarh(Lead/Lag) | -1 | 88160 | 87970 | 190 | -190 | -0.00019 | 423540 | 411610 | 11930 | -11930 | -0.01193
27 | AJMERI GATE | Q0263398 | SECURE | Kvarh(Lead/Lag) | -1 | 54720 | 53950 | 770 | -770 | -0.00077 | 656940 | 646180 | 10760 | -10760 | -0.01076
28 | NDLS | Q0263402 | SECURE | Kvarh(Lead/Lag) | -1 | 331100 | 325200 | 5900 | -5900 | -0.0059 | 2251800 | 2194800 | 57000 | -57000 | -0.057
DEV NAGAR
29 | 33KV RAMA ROAD | Q0487625 | SECURE | Kvarh(Lead/Lag) | -1 | -510000 | -364000 | -146000 | 146000 | 0.146 | 0 | 0 | 0 | 0 | 0
30 | 33KV SHAHZADA BAGH | Q0487626 | SECURE | Kvarh(Lead/Lag) | -1 | 615000 | 961000 | -346000 | 346000 | 0.346 | 0 | 0 | 0 | 0 | 0
31 | 33KV NARAINA DTC CKT-II | Q0487631 | SECURE | Kvarh(Lead/Lag) | -1 | -301000 | 0 | -301000 | 301000 | 0.301 | 0 | 0 | 0 | 0 | 0 | w.e.f 08-11-2023
FED FROM BYPL (RLY.)
31 | ANAND VIHAR | Q0430841 | SECURE | Kvarh(Lead/Lag) | -1200 | 23.89 | 23.86 | 0.03 | -36 | -3.6e-05 | 53.12 | 40.08 | 13.04 | -15648 | -0.015648
32 | THOMSON ROAD | Q0430833 | SECURE | Kvarh(Lead/Lag) | -1200 | 1.33 | 1.33 | 0 | 0 | 0 | 172.8 | 139.82 | 32.98 | -39576 | -0.039576
33 | SHIVAJI BRIDGE | Q0430835 | SECURE | Kvarh(Lead/Lag) | -1200 | 4 | 3.91 | 0.09 | -108 | -0.000108 | 43.84 | 42.26 | 1.58 | -1896 | -0.001896
34 | RRI HAMILTON RD. | Q0430822 | SECURE | Kvarh(Lead/Lag) | -1200 | 3.43 | 3.38 | 0.05 | -60 | -6e-05 | 48.91 | 46.83 | 2.08 | -2496 | -0.002496
35 | KODIYA PUL | Q0430828 | SECURE | Kvarh(Lead/Lag) | -3000 | 0.09 | 0.09 | 0 | 0 | 0 | 21.11 | 20.06 | 1.05 | -3150 | -0.00315
[10 empty] | 2.894 |  |  |  |  | -0.17602
NOVEMBER-2023
EXECUTIVE SUMMARY
ENERGY RELEASED TO CENTRAL
| 1) ENERGY AT 66/33/11 KV LEVEL (Refre A- Page -1) | [8 empty] | -16.7421 |  |  |  |  | -0.61411
| 2) INTER COMPANY EXCHANGE OF ENERGY AT 66/33/11 KV (Refer C Page-3) | [8 empty] | 2.894 |  |  |  |  | -0.17602
| 3) FROM ROHTAK ROAD (REFER ENERGY BALANCE SHEET ROHTAK ROAD ENCL.) | [8 empty] | 0 |  |  |  |  | 0
| TOTAL ENERGY TO BSES YAMUNA POWER LTD. - CENTRAL PART | [8 empty] | -13.8481 |  |  |  |  | -0.79013
ENERGY RELEASED TO EAST
| 1) ENERGY AT 66/33/11 KV LEVEL (Refre B- Page -2) | [8 empty] | -5.732 |  |  |  |  | -0.2165
| NET ENERGY TO BSES YAMUNA POWER LIMITED | [8 empty] | -19.5801 |  |  |  |  | -1.0066
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | -19.5801 | (REACTIVE MUs) |  |  |  | -1.0066 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | 5.4146 | (REACTIVE MUs) |  |  |  | 0.011439 | (REACTIVE MUs)
[9 empty] | TOTAL | -14.1655 | (REACTIVE MUs) |  |  |  | -0.99519 | (REACTIVE MUs)

## NDMC
DELHI TRANSCO LIMITED | [15 empty] | NOVEMBER-2023
REACTIVE ENERGY CONSUMPTION STATEMENT
CUSTOMER-NDMC
NDMC(+) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
AT PARK STREET
EXPORT TO NDMC
1 | BAIRD RD.1 | 4865107 | ELSTER | Kvarh(Lead/Lag) | 266.67 | 443 | 609 | -166 | -44267.22 | -0.044267 | 2146 | 2146 | 0 | 0 | 0
2 | BAIRD RD.2 | 4865150 | ELSTER | Kvarh(Lead/Lag) | 100 | 11937 | 11115 | 822 | 82200 | 0.0822 | 1603 | 1603 | 0 | 0 | 0
3 | NIRMAN BHAWAN | 4865136 | ELSTER | Kvarh(Lead/Lag) | 200 | 970608 | 971977 | -1369 | -273800 | -0.2738 | 244 | 244 | 0 | 0 | 0
4 | H.LANE | 4865172 | ELSTER | Kvarh(Lead/Lag) | 1000 | 568 | 701 | -133 | -133000 | -0.133 | 365 | 365 | 0 | 0 | 0
5 | 66 KV BD MARG-I | 4865010 | ELSTER | Kvarh(Lead/Lag) | 800 | 999972 | 1000008 | -36 | -28800 | -0.0288 | 1116 | 1115 | 1 | 800 | 0.0008
6 | 66 KV BD MARG-II | 4865004 | ELSTER | Kvarh(Lead/Lag) | 800 | 1594 | 1764 | -170 | -136000 | -0.136 | 2264 | 2265 | -1 | -800 | -0.0008
7 | 66KV DMRC-I | 4865050 | ELSTER | Kvarh(Lead/Lag) | 800 | 982119 | 982119 | 0 | 0 | 0 | 998603 | 998603 | 0 | 0 | 0
8 | 66KV DMRC-II | 4864998 | ELSTER | Kvarh(Lead/Lag) | 800 | 950267 | 950267 | 0 | 0 | 0 | 979419 | 979419 | 0 | 0 | 0
9 | 66KV GUEST HOUSE | 4864993 | ELSTER | Kvarh(Lead/Lag) | 800 | 940026 | 941412 | -1386 | -1108800 | -1.1088 | 987524 | 987526 | -2 | -1600 | -0.0016
10 | 66KV SCHOOL LANE | 5128403 | ELSTER | Kvarh(Lead/Lag) | 2000 | 992281 | 992327 | -46 | -92000 | -0.092 | 998064 | 998074 | -10 | -20000 | -0.02
I.P.STATION EXPORT TO NDMC
11 | BAY-2 (N BWN) | 4865161 | ELSTER | Kvarh(Lead/Lag) | 50 | 952668 | 952668 | 0 | 0 | 0 | 28639 | 30608 | -1969 | -98450 | -0.09845
12 | BAY-4 (E LANE) | 4865115 | ELSTER | Kvarh(Lead/Lag) | 100 | 998835 | 998839 | -4 | -400 | -0.0004 | 3180 | 3424 | -244 | -24400 | -0.0244
13 | BAY-6 (T MARG) | 4902512 | ELSTER | Kvarh(Lead/Lag) | 500 | 997774 | 997774 | 0 | 0 | 0 | 8955 | 9030 | -75 | -37500 | -0.0375
14 | BAY-10 (E LANE) | 4865121 | ELSTER | Kvarh(Lead/Lag) | 100 | 999817 | 999817 | 0 | 0 | 0 | 994493 | 995038 | -545 | -54500 | -0.0545
15 | BAY-16 (N BWN) | 4865129 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 998336 | 998336 | 0 | 0 | 0 | 4510 | 4548 | -38 | -50666.54 | -0.050667
16 | BAY-28 (C PLACE) | 4865159 | ELSTER | Kvarh(Lead/Lag) | 1000 | 11074 | 11074 | 0 | 0 | 0 | 43244 | 43244 | 0 | 0 | 0
17 | BAY-42 (C PLACE) | 4865122 | ELSTER | Kvarh(Lead/Lag) | 1333.33 | 999849 | 999849 | 0 | 0 | 0 | 4099 | 4108 | -9 | -11999.97 | -0.012
G.T.
19 | VIDYUT BHAWAN-1 | 4864996 | ELSTER | Kvarh(Lead/Lag) | 1000 | 989726 | 990736 | -1010 | -1010000 | -1.01 | 399 | 399 | 0 | 0 | 0
20 | VIDYUT BHAWAN-2 | 4865000 | ELSTER | Kvarh(Lead/Lag) | 1000 | 974502 | 975515 | -1013 | -1013000 | -1.013 | 3090 | 3090 | 0 | 0 | 0
21 | SCHOOL LANE-1 | 4865028 | ELSTER | Kvarh(Lead/Lag) | 1000 | 989426 | 989772 | -346 | -346000 | -0.346 | 352 | 352 | 0 | 0 | 0 | Check Data upto 14.11.23
|  | 4864851 | ELSTER | Kvarh(Lead/Lag) | 2500 | 999808 | 1000000 | -192 | -480000 | -0.48 | 999999 | 1000000 | -1 | -2500 | -0.0025 | w.e.f 14-11-2023
22 | SCHOOL LANE-2 | 4864885 | ELSTER | Kvarh(Lead/Lag) | 2500 | 992527 | 993151 | -624 | -1560000 | -1.56 | 512 | 512 | 0 | 0 | 0
[10 empty] | -4.409 |  |  |  |  | -0.0025
RIDGE VALLEY
23 | SPM NO.1/ BAPUDHAM | 4864955 | ELSTER | Kvarh(Lead/Lag) | 1000 | 988757 | 989277 | -520 | -520000 | -0.52 | 2698 | 2698 | 0 | 0 | 0
24 | SPM NO.2 | 4864820 | ELSTER | Kvarh(Lead/Lag) | 160 | 2683 | 2829 | -146 | -23360 | -0.02336 | 45949 | 45980 | -31 | -4960 | -0.00496
25 | NEHRU PARK | 4864811 | ELSTER | Kvarh(Lead/Lag) | 200 | 3832 | 3859 | -27 | -5400 | -0.0054 | 27028 | 27041 | -13 | -2600 | -0.0026
26 | Guest House | 4864961 | ELSTER | Kvarh(Lead/Lag) | 1000 | 967174 | 967906 | -732 | -732000 | -0.732 | 999625 | 999625 | 0 | 0 | 0
A.I.I.M.S.
27 | KILOKARI | 4865103 | ELSTER | Kvarh(Lead/Lag) | -833.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | SIRI FORT | 4865114 | ELSTER | Kvarh(Lead/Lag) | -833.33 | 0 | 0 | 0 | 0 | 0 | 999871 | 999871 | 0 | 0 | 0
29 | RIDGE VALLEY | 4902508 | ELSTER | Kvarh(Lead/Lag) | -833.33 | 359 | 241 | 118 | -98332.94 | -0.098333 | 7131 | 7032 | 99 | -82499.67 | -0.0825
NOVEMBER-2023
NDMC(+) Continue…
TRAUMA CENTRE
30 | 33KV TX-1 | 5100234 | ELSTER | Kvarh(Lead/Lag) | -1000 | 996193 | 997793 | -1600 | 1600000 | 1.6 | 999999 | 1000000 | -1 | 1000 | 0.001
31 | 33KV TX-2 | 4864940 | ELSTER | Kvarh(Lead/Lag) | -1000 | 11270 | 7119 | 4151 | -4151000 | -4.151 | 995100 | 995100 | 0 | 0 | 0
ELECTRIC LANE
32 | 33KV TX-1 | 4864891 | ELSTER | Kvarh(Lead/Lag) | -2000 | 998293 | 998284 | 9 | -18000 | -0.018 | 994585 | 994585 | 0 | 0 | 0
33 | 33KV TX-2 | 4865005 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999758 | 999783 | -25 | 25000 | 0.025 | 998752 | 998752 | 0 | 0 | 0
KIDWAI NAGAR
34 | I/C from R.Valley at kidwai ngr | 4864850 | ELSTER | Kvarh(Lead/Lag) | 625 | 472 | 455 | 17 | 10625 | 0.010625 | 8186 | 8083 | 103 | 64375 | 0.064375
LODHI ROAD
35 | SHAN NAGAR 1 | 4902580 | ELSTER | Kvarh(Lead/Lag) | 100 | 923 | 903 | 20 | 2000 | 0.002 | 3610 | 3604 | 6 | 600 | 0.0006
36 | SHAN NAGAR 2 | 4902544 | ELSTER | Kvarh(Lead/Lag) | 100 | 5830 | 5686 | 144 | 14400 | 0.0144 | 5938 | 5935 | 3 | 300 | 0.0003
37 | 33KV SAHJAHAN ROAD | 4864793 | ELSTER | Kvarh(Lead/Lag) | 200 | 999457 | 999926 | -469 | -93800 | -0.0938 | 999703 | 999703 | 0 | 0 | 0
TILAK MARG
38 | EXHB-II | 4865151 | ELSTER | Kvarh(Lead/Lag) | 500 | 21875 | 21883 | -8 | -4000 | -0.004 | 6207 | 6211 | -4 | -2000 | -0.002
NDMC(-) | [7 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
TRAUMA CENTRE
1 | 33KV Bhikaji Cama Place | 4864839 | ELSTER | Kvarh(Lead/Lag) | -1000 | 758 | 950 | -192 | 192000 | 0.192 | 999777 | 999777 | 0 | 0 | 0
2 | 33KV IIT Circuit | 4864872 | ELSTER | Kvarh(Lead/Lag) | -1000 | 996074 | 996765 | -691 | 691000 | 0.691 | 999564 | 999564 | 0 | 0 | 0
AIIMS
3 | 11KV VIKAS SADAN | 4865072 | ELSTER | Kvarh(Lead/Lag) | -100 | 999830 | 999916 | -86 | 8600 | 0.0086 | 999678 | 999678 | 0 | 0 | 0
4 | 11KV NDSE | 4865066 | ELSTER | Kvarh(Lead/Lag) | -200 | 237 | 159 | 78 | -15600 | -0.0156 | 407 | 407 | 0 | 0 | 0
TOTAL ENERGY RELEASED AT 66/33/11 KV LEVEL | [9 empty] | -9.2617 |  |  |  |  | -0.3274
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
| ENERGY TO NDMC | [8 empty] | -9.2617 |  |  |  |  | -0.3274
| SHARED DISTRIBUTION GENERATED BY GENCO | [8 empty] | 1.221 |  |  |  |  | 0.0023972
| TOTAL ENERGY TO NDMC | [8 empty] | -8.0408 |  |  |  |  | -0.325

## MES
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | NOVEMBER-2023
CUSTOMER- MES
[8 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
MES(+)
FED FROM DTL SYSTEM.
NARAINA ( ON 33KV)
1 | KHBR LANE-1-EXP. | 5128430 | ELSTER | Kvarh(Lead/Lag) | 200 | 4171 | 4303 | -132 | -26400 | -0.0264 | 82181 | 82181 | 0 | 0 | 0
2 | KHBR LANE-2 -EXP. | 4864819 | ELSTER | Kvarh(Lead/Lag) | 160 | 999720 | 999772 | -52 | -8320 | -0.00832 | 32963 | 32964 | -1 | -160 | -0.00016
3 | KIRBY PLACE-1 | 4864815 | ELSTER | Kvarh(Lead/Lag) | 200 | 999878 | 999879 | -1 | -200 | -0.0002 | 2281 | 2307 | -26 | -5200 | -0.0052
4 | KIRBY PLACE-2 | 4864918 | ELSTER | Kvarh(Lead/Lag) | 400 | 999751 | 999783 | -32 | -12800 | -0.0128 | 20104 | 20106 | -2 | -800 | -0.0008
5 | SHEKHAWATI- 1 | 4864894 | ELSTER | Kvarh(Lead/Lag) | 800 | 999265 | 999267 | -2 | -1600 | -0.0016 | 743 | 743 | 0 | 0 | 0
6 | SHEKHAWATI- 2 | 5128425 | ELSTER | Kvarh(Lead/Lag) | 400 | 2246 | 2289 | -43 | -17200 | -0.0172 | 6794 | 6805 | -11 | -4400 | -0.0044
RIDGE VALLEY ON 33KV
7 | KHBR LANE-1 -EXP | 4865164 | ELSTER | Kvarh(Lead/Lag) | 666.667 | 999667 | 999795 | -128 | -85333.376 | -0.085333 | 519 | 557 | -38 | -25333.346 | -0.025333
8 | KHBR LANE-2 -EXP. | 4864845 | ELSTER | Kvarh(Lead/Lag) | 1000 | 1064 | 1105 | -41 | -41000 | -0.041 | 369 | 366 | 3 | 3000 | 0.003
9 | 33KV R R HOSPITAL | Q0819156 | SECURE | Kvarh(Lead/Lag) | 2 | 0 | 0 | 0 | 0 | 0 | 30500 | -800 | 31300 | 62600 | 0.0626 | w.e.f 19-10-23
| TOTAL FED FROM DTL SYSTEM. | [8 empty] | -0.19285 |  |  |  |  | 0.029707
FED FROM BSES RAJDHANI POWER LIMITED (11KV)
10 | R.R. HOSPITAL | 4902594 | ELSTER | Kvarh(Lead/Lag) | 500 | 109 | 93 | 16 | 8000 | 0.008 | 792 | 785 | 7 | 3500 | 0.0035
11 | DEFENCE CLUB | 4865067 | ELSTER | Kvarh(Lead/Lag) | 100 | 105 | 88 | 17 | 1700 | 0.0017 | 1849 | 1846 | 3 | 300 | 0.0003
12 | SUBROTO PARK | 4902562 | ELSTER | Kvarh(Lead/Lag) | 75 | 4831 | 4693 | 138 | 10350 | 0.01035 | 73704 | 73089 | 615 | 46125 | 0.046125
13 | SUBROTO PARK | 4865088 | ELSTER | Kvarh(Lead/Lag) | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | BI LINES | 4902552 | ELSTER | Kvarh(Lead/Lag) | 75 | 784 | 784 | 0 | 0 | 0 | 6011 | 6011 | 0 | 0 | 0
15 | BI LINES | 4865075 | ELSTER | Kvarh(Lead/Lag) | 100 | 10294 | 10294 | 0 | 0 | 0 | 8853 | 8853 | 0 | 0 | 0
| TOTAL FED FROM BSES RAJDHANI POWER LIMITED (11KV) | [8 empty] | 0.02005 |  |  |  |  | 0.049925
| TOTAL FED FROM DTL SYSTEM. | [8 empty] | -0.19285 |  |  |  |  | 0.029707
| GRAND TOTAL (BSES RPL+NDPL+DTL) | [8 empty] | -0.1728 |  |  |  |  | 0.079632
NET REACTIVE ENERGY CHARGEABLE
[10 empty] | Energy for above 103% |  |  |  |  | Energy for below 97%
EXPORT IN LAGGING/LEADING MODE FROM THE SOURCE | [9 empty] | -0.1728 | (REACTIVE MUs) |  |  |  | 0.079632 | (REACTIVE MUs)
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | 0.020637 | (REACTIVE MUs) |  |  |  | 0 | (REACTIVE MUs)
[9 empty] | TOTAL | -0.15217 | (REACTIVE MUs) |  |  |  | 0.079632 | (REACTIVE MUs)

## Railway
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | NOVEMBER-2023
CUSTOMER- NORTHERN RAILWAYS
[8 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
RAILWAY(+)
FED FROM DTL SYSTEM.
NARELA DSIDC-1
1 | 66KV Rly Ckt-1 | 4864952 | ELSTER | Kvarh(Lead/Lag) | 625 | 992095 | 992000 | 95 | 59375 | 0.059375 | 1346 | 1343 | 3 | 1875 | 0.001875
2 | 66KV Rly Ckt-2 | 4865039 | ELSTER | Kvarh(Lead/Lag) | 500 | 999688 | 999716 | -28 | -14000 | -0.014 | 801 | 796 | 5 | 2500 | 0.0025
RIDGE VALLEY
1 | 66KV Rly Ckt-1 | 4864994 | ELSTER | Kvarh(Lead/Lag) | 800 | 2437 | 1898 | 539 | 431200 | 0.4312 | 1593 | 1593 | 0 | 0 | 0
FED FROM BYPL (RLY.)
1 | SADAR | Q0263400 | SECURE | Kvarh(Lead/Lag) | 1 | 88160 | 87970 | 190 | 190 | 0.00019 | 423540 | 411610 | 11930 | 11930 | 0.01193
2 | AJMERI GATE | Q0263398 | SECURE | Kvarh(Lead/Lag) | 1 | 54720 | 53950 | 770 | 770 | 0.00077 | 656940 | 646180 | 10760 | 10760 | 0.01076
3 | NDLS | Q0263402 | SECURE | Kvarh(Lead/Lag) | 1 | 331100 | 325200 | 5900 | 5900 | 0.0059 | 2251800 | 2194800 | 57000 | 57000 | 0.057
4 | ANAND VIHAR | Q0430841 | SECURE | Kvarh(Lead/Lag) | 1200 | 23.89 | 23.86 | 0.03 | 36 | 3.6e-05 | 53.12 | 40.08 | 13.04 | 15648 | 0.015648
5 | THOMSON ROAD | Q0430833 | SECURE | Kvarh(Lead/Lag) | 1200 | 1.33 | 1.33 | 0 | 0 | 0 | 172.8 | 139.82 | 32.98 | 39576 | 0.039576
6 | SHIVAJI BRIDGE | Q0430835 | SECURE | Kvarh(Lead/Lag) | 1200 | 4 | 3.91 | 0.09 | 108 | 0.000108 | 43.84 | 42.26 | 1.58 | 1896 | 0.001896
7 | RRI HAMILTON RD. | Q0430822 | SECURE | Kvarh(Lead/Lag) | 1200 | 3.43 | 3.38 | 0.05 | 60 | 6e-05 | 48.91 | 46.83 | 2.08 | 2496 | 0.002496
8 | KODIYA PUL | Q0430828 | SECURE | Kvarh(Lead/Lag) | 3000 | 0.09 | 0.09 | 0 | 0 | 0 | 21.11 | 20.06 | 1.05 | 3150 | 0.00315
FED FROM BRPL(RLY.)
9 | NIZAMUDDIN RLY STN | Q0430831 | SECURE | Kvarh(Lead/Lag) | 600 | 0.12 | 0.12 | 0 | 0 | 0 | 48.08 | 45.88 | 2.2 | 1320 | 0.00132
10 | TUGLUKABAD RLY STN | Q0430821 | SECURE | Kvarh(Lead/Lag) | 3000 | 0.49 | 0.34 | 0.15 | 450 | 0.00045 | 27.09 | 25.3 | 1.79 | 5370 | 0.00537
| TOTAL FED FROM DTL SYSTEM. | [8 empty] | 0.48409 |  |  |  |  | 0.15352
SHARED DISTRIBUTION GENERATED BY GENCO | [9 empty] | 0.0089889 |  |  |  |  | 0
TOTAL ENERGY TO Northern Railway | [9 empty] | 0.49308 |  |  |  |  | 0.15352

## ROHTAK ROAD
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | NOVEMBER-2023
ROHTAK ROAD
[8 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
TO BSES RAJDHANI
AT 33 KV LEVEL
1 | O/G SBMILL-1 | 4865155 | ELSTER | Kvarh(Lead/Lag) | 500 | 992345 | 992775 | -430 | -215000 | -0.215 | 999251 | 999251 | 0 | 0 | 0
2 | O/G SBMILL-2 | 4864794 | ELSTER | Kvarh(Lead/Lag) | 100 | 16528 | 17934 | -1406 | -140600 | -0.1406 | 986604 | 986609 | -5 | -500 | -0.0005
3 | O/G VISHAL-1 | 4865100 | ELSTER | Kvarh(Lead/Lag) | 833.333 | 343 | 426 | -83 | -69166.639 | -0.069167 | 294 | 294 | 0 | 0 | 0
4 | O/G MADI PUR | 4864863 | ELSTER | Kvarh(Lead/Lag) | 937.5 | 997161 | 997209 | -48 | -45000 | -0.045 | 998813 | 998813 | 0 | 0 | 0
AT 33/11 KV LEVEL
5 | TX.-I | 5252046 | ELSTER | Kvarh(Lead/Lag) | -1000 | 999114 | 999117 | -3 | 3000 | 0.003 | 998644 | 998645 | -1 | 1000 | 0.001
6 | TX-II | [8 empty] | -0.0224 |  |  |  |  | 0 | Assessment(01.11.23 To 09.11.23)
|  | 4902535 | ELSTER | Kvarh(Lead/Lag) | -1500 | 41 | 0 | 41 | -61500 | -0.0615 | 0 | 0 | 0 | 0 | 0 | w.e.f 09-11-2023
7 | B/C (IMP.TO BRPL) | 4902559 | ELSTER | Kvarh(Lead/Lag) | 300 | 210 | 210 | 0 | 0 | 0 | 999957 | 999957 | 0 | 0 | 0
| TOTAL BSES RAJDHANI PO.LTD. | [8 empty] | -0.55067 |  |  |  |  | 0.0005
TO BSES YAMUNA PO. LTD.
AT 33 KV LEVEL
8 | O/G FAIZ ROAD | 4864796 | ELSTER | Kvarh(Lead/Lag) | 200 | 954745 | 954745 | 0 | 0 | 0 | 991368 | 991368 | 0 | 0 | 0
9 | O/G DMS | 4864804 | ELSTER | Kvarh(Lead/Lag) | 187.5 | 993263 | 993263 | 0 | 0 | 0 | 993619 | 993619 | 0 | 0 | 0
| TOTAL (BSES Y.P.L.) | [8 empty] | 0 |  |  |  |  | 0
TO NORTH DELHI POWER LIMITED
AT 33 KV LEVEL
10 | O/G VISHAL-2 | 4864866 | ELSTER | Kvarh(Lead/Lag) | 1250 | 999047 | 999216 | -169 | -211250 | -0.21125 | 998445 | 998445 | 0 | 0 | 0
11 | O/G 33KV RAMPURA-1 | 5295199 | ELSTER | Kvarh(Lead/Lag) | 937.5 | 997945 | 998255 | -310 | -290625 | -0.29063 | 999314 | 999314 | 0 | 0 | 0
12 | O/G 33KV RAMPURA-2 | 4864814 | ELSTER | Kvarh(Lead/Lag) | 125 | 990512 | 992683 | -2171 | -271375 | -0.27137 | 994240 | 994247 | -7 | -875 | -0.000875
13 | O/G 33KV RAMA ROAD | 4865123 | ELSTER | Kvarh(Lead/Lag) | 1250 | 999021 | 999176 | -155 | -193750 | -0.19375 | 999939 | 999939 | 0 | 0 | 0
14 | O/G 33KV SH.W.BAGH-2 | 4865152 | ELSTER | Kvarh(Lead/Lag) | 1000 | 997825 | 997952 | -127 | -127000 | -0.127 | 999482 | 999483 | -1 | -1000 | -0.001
15 | O/G 33KV KIRTI NAGAR | 4864821 | ELSTER | Kvarh(Lead/Lag) | 1000 | 963240 | 965059 | -1819 | -1819000 | -1.819 | 988754 | 988753 | 1 | 1000 | 0.001
AT 33/11 KV LEVEL
16 | TX-III | 5128406 | ELSTER | Kvarh(Lead/Lag) | -625 | 999484 | 999545 | -61 | 38125 | 0.038125 | 999740 | 999740 | 0 | 0 | 0
17 | B/C (IMP.TO NDPL) | 4902559 | ELSTER | Kvarh(Lead/Lag) | -300 | 210 | 210 | 0 | 0 | 0 | 999957 | 999957 | 0 | 0 | 0
| TOTAL NDPL | [8 empty] | -2.8749 |  |  |  |  | -0.000875
| E) NET EXPORT TO BSES RPL | [8 empty] | -0.55067 |  |  |  |  | 0.0005
| F) NET EXPORT TO BSES YPL | [8 empty] | 0 |  |  |  |  | 0
| G) NET EXPORT TO N.D.P.L. | [8 empty] | -2.8749 |  |  |  |  | -0.000875

## STEPPED UP GENCO
DELHI TRANSCO LIMITED
REACTIVE ENERGY CONSUMPTION STATEMENT | [14 empty] | NOVEMBER-2023
A.) EXPORT/IMPORT OF REACTIVE ENERGY IN LEAD/LAG MODE ON IBT's AT GENCO
[8 empty] | DELIVERED & RECEIVED ABOVE 103% |  |  |  |  | DELIVERED & RECEIVED BELOW 97 %
Sr. No. | STATION / FEEDER | METER NO. | MAKE | UNIT | M.F. (O/A) | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | FINAL READING 30/11/2023 | INTIAL READING 01/11/2023 | DIFF. | CONSP. | REACTIVE MUs | REMARK
A) | G.T.
| (66KV ) | (EXPORT)
1 | IBT-I | 4865015 | ELSTER | kvarh (Lead/lag) | 2000 | 20626 | 17930 | 2696 | 5392000 | 5.392 | 999980 | 999980 | 0 | 0 | 0
2 | IBT-2 | 4864969 | ELSTER | kvarh (Lead/lag) | 2000 | 11628 | 8948 | 2680 | 5360000 | 5.36 | 999976 | 999976 | 0 | 0 | 0
[7 empty] | Total Generation at GT(IBT1+IBT2) = |  |  | 10.752 |  |  |  |  | 0
[7 empty] | Generation at feeders |  | = | -10.4672 |  |  |  |  | -0.0025
[7 empty] | NET REACTIVE ENERGY at GT = |  |  | 21.2193 |  |  |  |  | 0.0025
Reactive Energy distribution to DISCOMs in proportion to their allocation for GT:
| NDPL | (DERC order = |  |  |  | 29.67 | % |  |  | 6.2958 |  |  |  |  | 0.00074175
| BRPL | (DERC order = |  |  |  | 41.53 | % |  |  | 8.8124 |  |  |  |  | 0.0010383
| BYPL | (DERC order = |  |  |  | 22.74 | % |  |  | 4.8253 |  |  |  |  | 0.0005685
| NDMC | (DERC order = |  |  |  | 4.95 | % |  |  | 1.0504 |  |  |  |  | 0.00012375
| MES | (DERC order = |  |  |  | 0 | % |  |  | 0 |  |  |  |  | 0
| N.Railway | (DERC order = |  |  |  | 0 | % |  |  | 0 |  |  |  |  | 0
B) | MSW BAWANA
1 | MSW BAWANA | 4864884 | ELSTER | kvarh (Lead/lag) | -1000 | 997721 | 998815 | -1094 | 1094000 | 1.094 | 999499 | 999507 | -8 | 8000 | 0.008
[6 empty] | NET REACTIVE ENERGY at MSW BAWANA = |  |  |  | 1.094 |  |  |  |  | 0.008
Reactive Energy distribution to DISCOMs in proportion to their allocation for MSW-BAWANA:
| NDPL | (DERC order = |  |  |  | 29.2 | % |  |  | 0.31945 |  |  |  |  | 0.002336
| BRPL | (DERC order = |  |  |  | 41.81 | % |  |  | 0.4574 |  |  |  |  | 0.0033448
| BYPL | (DERC order = |  |  |  | 23.9 | % |  |  | 0.26147 |  |  |  |  | 0.001912
| NDMC | (DERC order = |  |  |  | 5.09 | % |  |  | 0.055685 |  |  |  |  | 0.0004072
| MES | (DERC order = |  |  |  | 0 | % |  |  | 0 |  |  |  |  | 0
| N.Railway | (DERC order = |  |  |  | 0 | % |  |  | 0 |  |  |  |  | 0
C) | PRAGATI
| (220 KV) | (EXPORT)
1 | GT-I | 5100238 | ELSTER | kvarh (lag) | -750 | 195476 | 194797 | 679 | -509250 | -0.50925 | 999741 | 999741 | 0 | 0 | 0
2 | GT-II | 4902490 | ELSTER | kvarh (lag) | -1000 | 8179 | 7803 | 376 | -376000 | -0.376 | 4 | 4 | 0 | 0 | 0
3 | STG | 4902483 | ELSTER | kvarh (lag) | -750 | 991611 | 993044 | -1433 | 1074750 | 1.0748 | 999402 | 999402 | 0 | 0 | 0
[8 empty] | NET REACTIVE ENERGY at PRAGATI = |  | 0.1895 |  |  |  |  | 0
Reactive Energy distribution to DISCOMs in proportion to their allocation for PRAGATI :
| NDPL | (DERC order = |  |  |  | 19.28 | % |  |  | 0.036536 |  |  |  |  | 0
| BRPL | (DERC order = |  |  |  | 28.29 | % |  |  | 0.05361 |  |  |  |  | 0
| BYPL | (DERC order = |  |  |  | 16.07 | % |  |  | 0.030453 |  |  |  |  | 0
| NDMC | (DERC order = |  |  |  | 30.3 | % |  |  | 0.057419 |  |  |  |  | 0
| MES | (DERC order = |  |  |  | 6.06 | % |  |  | 0.011484 |  |  |  |  | 0
| N.Railway | (DERC order = |  |  |  | 0 | % |  |  | 0 |  |  |  |  | 0
D) | EAST DELHI WASTE - Ghazipur
1 | E.Delhi Waste GZP | 5295115 | ELSTER | kvarh (Lead/lag) | -100 | 292629 | 304973 | -12344 | 1234400 | 1.2344 | 984104 | 984104 | 0 | 0 | 0
[8 empty] | NET REACTIVE ENERGY at EDWMP = |  | 1.2344 |  |  |  |  | 0
Reactive Energy distribution to DISCOMs in proportion to their Active Energy drawl(week No- 35 FY2023-24) for EDWMP-GHAZIPUR :
| NDPL | (ACTIVE ENERGY DRAWL= |  |  |  | 32.6123 | % |  |  | 0.40257 |  |  |  |  | 0
| BRPL | (ACTIVE ENERGY DRAWL= |  |  |  | 41.163 | % |  |  | 0.50812 |  |  |  |  | 0
| BYPL | (ACTIVE ENERGY DRAWL= |  |  |  | 20.7861 | % |  |  | 0.25658 |  |  |  |  | 0
| NDMC | (ACTIVE ENERGY DRAWL= |  |  |  | 3.9689 | % |  |  | 0.048992 |  |  |  |  | 0
| MES | (ACTIVE ENERGY DRAWL= |  |  |  | 0.7415 | % |  |  | 0.0091531 |  |  |  |  | 0
| N.Railway | (ACTIVE ENERGY DRAWL= |  |  |  | 0.7282 | % |  |  | 0.0089889 |  |  |  |  | 0
E) | TEKHAND WASTE TO ENERGY PANT
1 | TEKHAND WASTE TO ENERGY PANT | Q0473785 | SECURE | kvarh (Lead/lag) | -240000 | -2.48 | -1.75 | -0.73 | 175200 | 0.1752 | -28.44 | -28.28 | -0.16 | 38400 | 0.0384
Reactive Energy distribution to DISCOMs in proportion to their allocation for MSW-BAWANA:
| NDPL | (DERC order = |  |  |  | 30.09 | % |  |  | 0.052718 |  |  |  |  | 0.011555
| BRPL | (DERC order = |  |  |  | 41.72 | % |  |  | 0.073093 |  |  |  |  | 0.01602
| BYPL | (DERC order = |  |  |  | 23.33 | % |  |  | 0.040874 |  |  |  |  | 0.0089587
| NDMC | (DERC order = |  |  |  | 4.86 | % |  |  | 0.0085147 |  |  |  |  | 0.0018662
| MES | (DERC order = |  |  |  | 0 | % |  |  | 0 |  |  |  |  | 0
| N.Railway | (DERC order = |  |  |  | 0 | % |  |  | 0 |  |  |  |  | 0
F) | TOTAL REACTIVE ENRGY DISTRIBUTION OF EACH DISCOM ON DELHI GENERATORS (A+B+C+D+E)
1) | NDPL |  |  |  | = |  |  |  |  | 7.107 |  |  |  |  | 0.014632
2) | BRPL |  |  |  | = |  |  |  |  | 9.9046 |  |  |  |  | 0.020404
3) | BYPL |  |  |  | = |  |  |  |  | 5.4146 |  |  |  |  | 0.011439
4) | NDMC |  |  |  | = |  |  |  |  | 1.221 |  |  |  |  | 0.0023972
5) | MES |  |  |  | = |  |  |  |  | 0.020637 |  |  |  |  | 0
6) | N.Railway |  |  |  | = |  |  |  |  | 0.0089889 |  |  |  |  | 0

## FINAL EX. SUMMARY
DELHI TRANSCO LIMITED
REACTIVE ENERGY RELEASE STATEMENT TO LICENSEES.
PERIOD 1st NOVEMBER-2023 TO 30th NOVEMBER-2023
FINAL EXECUTIVE SUMMERY
[6 empty] | Energy for above 103% |  | Energy for below 97%
1 | NET REACTIVE ENERGY TO N.D.P.L. |  |  |  |  | -52.332 |  | -0.9437
2 | NET REACTIVE ENERGY TO BSES RAJDHANI PO.LTD. |  |  |  |  | -38.7375 |  | -3.1406
3 | NET REACTIVE ENERGY TO BSES YAMUNA PO.LTD. |  |  |  |  | -14.1655 |  | -0.99519
4 | NET REACTIVE ENERGY TO NDMC |  |  |  |  | -8.0408 |  | -0.325
5 | NET REACTIVE ENERGY TO MES |  |  |  |  | -0.15217 | + | 0.079632
6 | NET REACTIVE ENERGY TO N. RAILWAYS |  |  |  | + | 0.49308 | + | 0.15352
ALL FIGURES IN Mus.
Note:-
+ve sign indicates reactive energy drawl from the grid/system
-ve sign indicates reactive energy injected to the grid/system
Note:-Above Data is provided by DTL Metering Department