## Sheet1
Self certification of UFRs and df/dt relays testing carried out by STUs for the 2nd Quarter (July-Sept.)of 2015-16
Name of State Control Area:Delhi
S.No. | Name of S/Stn (including voltage level) | Name of Feeder/ transformer (including voltage level) | Affected Area | Estimated Load relief(MW) | Minimum Load on the feeder (MW) | Whether the feeder is radial | Whether this feeder/underlying feeders are a part of scheduled power cuts/load shedding | Whether this feeder /under lying feeders covered under UFR | Whether this feeder /under lying feeders covered under df/dt shedding scheme | Whether the feeder/under lying feeders covered under any SPS? | UFR(Hz) or df/dt(Hz/sec.) setting | Whether power flow and breaker status of the feeder/underlying feeder visible in SLDC through SCADA | Whether relay is Numerical | Model and Make of relay | Date and time when relay/load relief /operation checked last time | Name and Dignation of the checking officer
1 | 220KV KASHMIRI GATE | 33KV Fountain CKT.No. I |  | 15 | 3.75 | Yes | No | yes | No | No | 49.2Hz | yes | yes | P143,Alstom Make | 26.06.15 | Mr. Avishek Kumar Mallick, Asstt. Manager
|  | 11KV I.S.B.T. Flyover |  | 1.577 | 0.39425 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV New Kashmiri Gate |  | 1.995 | 0.49875 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV Mahavir icefactory |  | 3.04 | 0.76 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV G.P.O. |  | 2.185 | 0.54625 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV Lohori Gate |  | 20 | 5 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV Hamilton Road |  | 2.375 | 0.59375 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV Bela Road |  | 0.76 | 0.19 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV Ludlocastle |  | 2.28 | 0.57 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33KV Jama Masjid |  | 22 | 5.5 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV Metcalf House |  | 3.04 | 0.76 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
2 | 220kV SOW | 66 KV YAMUNA VIHAR -1 |  | 50.16 | 12.54 | Yes | No | yes | No | No | 49.2Hz | yes | yes | P143,Alstom Make | 27.06.15 | Mr. Avishek Kumar Mallick, Asstt. Manager
|  | 66 KV YAMUNA VIHAR -2 |  | 50.16 | 12.54 | Yes | No | yes | No | No | 49.2Hz | yes | yes
|  | 66 KV GHONDA -I |  | 46.74 | 11.685 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66 KV GHONDA -II |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66 KV SHASTRI PARK-I |  | 41.04 | 10.26 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 66 KV SHASTRI PARK-II |  | 29.64 | 7.41 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV O/G TUKHMEERPUR |  | 1.615 | 0.40375 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV O/G B BLK. BHAJANPURA |  | 4.085 | 1.0212 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV O/G MONI BABA MANDIR |  | 1.33 | 0.3325 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV O/G SHAHDRA BANDH |  | 1.995 | 0.49875 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV O/G 3 1/2 PUSHTA VIJAY COLONY |  | 2.28 | 0.57 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV O/G D-BLOCK GAWARI EXTN |  | 2.66 | 0.665 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV O/G WAZIRABAD SWITCHING STATION-II |  | 1.045 | 0.26125 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV O/G SADATPUR |  | 4.94 | 1.235 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
3 | 220KV GEETA COLONY | 33KV KANTI NG.-I |  | 10.8025 | 2.7006 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143,Alstom Make | 13.06.15 | Ms Twinkle Gupta, Asstt. Manager
|  | 33KV KANTI NG.-II |  | 13.7746 | 3.4436 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 33KV SHAKAR PUR |  | 8.6877 | 2.1719 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV GEETA CLY-I |  | 15.2607 | 3.8152 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 33KV GEETA CLY-II |  | 28.1208 | 7.0302 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 33KV KAILASH CLY-I |  | 8 | 2 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33KV KAILASH CLY-II |  | 8 | 2 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
4 | 220KV PATPARGANJ | 66KV VIVEK VHR-I |  | 52 | 13 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes | P143,Alstom Make | 14.06.15 | Ms Twinkle Gupta, Asstt. Manager
|  | 66KV VIVEK VHR-II |  | 52 | 13 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 66KV GH-I |  | 29 | 7.25 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 66KV GH-II |  | 29 | 7.25 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 33KV GURU ANGAD NG.-I |  | 20.2904 | 5.0726 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV GURU ANGAD NG.-II |  | 17.1468 | 4.2867 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV CBD |  | 32.5789 | 8.1447 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 33KV PREET VHR |  | 23.43 | 5.8575 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV IDC |  | 2.0005 | 0.50011 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV COMMERCIAL |  | 1.9052 | 0.4763 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV PREET VHR |  | 1.4 | 0.35 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV SHAKARPUR |  | 2.7625 | 0.69063 | Yes | No | yes | No | No | 48.6Hz | yes | yes
5 | 220KV NAJAFGARH | 66kv jaffar pur -I |  | 6.65 | 1.6625 | Yes | No | yes | No | No | 48.6Hz | yes | yes | P143,Alstom Make | 11.07.15 | Mohd. Ansar, Asstt. Manager
|  | 66KV jaffar pur -II |  | 26.61 | 6.6525 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 66KV,20MVA TX.3 |  | 14.41 | 3.6025 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 66KV Budela-I |  | 59.88 | 14.97 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 66KV Budela-II |  | 59.88 | 14.97 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11kV Chhawala |  | 7 | 1.75 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11kVRama Park |  | 1.85 | 0.4625 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11kV Deenpur |  | 3.7 | 0.925 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11kv TP KOTLA |  | 3.7 | 0.925 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11kv Nangli Sakarwati |  | 4.25 | 1.0625 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11kv Anaj Mandi |  | 4.16 | 1.04 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11kv Najafgarh-I |  | 5.27 | 1.3175 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11kV Dhichau Kalan |  | 4.8 | 1.2 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11kv Nangli Sakarwati |  | 4.25 | 1.0625 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11kv Seven panel |  | 3.33 | 0.8325 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11kv Kakrola |  | 5.54 | 1.385 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11kV Chhawala |  | 7 | 1.75 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11kVRama Park |  | 1.85 | 0.4625 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
6 | 220KV PAPPANKALAN-1 | 66KV G-2 CKT-1 |  | 64.31 | 16.0775 | Yes | No | yes | No | No | 49.2Hz | yes | yes | P143, Alstom Make | 10.07.15 | Mohd. Ansar, Asstt. Manager
|  | 66KV G-2 CKT-II |  | 64.31 | 16.0775 | Yes | No | yes | No | No | 49.2Hz | yes | yes
|  | 66KV binda pur-I |  | 19.4 | 4.85 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66KV binda pur-II |  | 19.4 | 4.85 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66KV G-6 CKT-I |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66KV G-6 CKT-II |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66KV REWARI LINE |  | 46.02 | 11.505 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV PP-1 |  | 1.94 | 0.485 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV MAHA LUXMI |  | 3.14 | 0.785 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV MANGALPURI |  | 3.88 | 0.97 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV NSIT |  | 2.13 | 0.5325 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV PP-II |  | 1.94 | 0.485 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV BENGALI CLY |  |  | 0 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV I/C NO.2 |  | 15.34 | 3.835 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV SEC.2 PPK |  | 2.4 | 0.6 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV PALAM VILL |  | 3.05 | 0.7625 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV SEC-7 |  | 3.97 | 0.9925 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV EVER GREEN |  | 3.6 | 0.9 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV VINOD PURI |  |  | 0 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV C-2 MAHAVIR ENCL |  | 4.9 | 1.225 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV I/C NO.3 |  | 17.93 | 4.4825 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV NASEER PUR |  | 3.88 | 0.97 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV SEC-10PPK |  | 3.23 | 0.8075 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV SEC-19 |  | 2.86 | 0.715 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
7 | 220KV LODHI ROAD | 33KV nizamuddin |  | 11.09 | 2.7725 | Yes | No | yes | No | No | 48.8Hz | yes | yes | P143, Alstom Make | 26.06.15 | Mr. Arpit Agarwal, Asstt. Manager
|  | 33KV J.L.N. Stadium |  | 0 | 0 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV Defence colony-II |  | 25.5 | 6.375 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 33KV India habitat cen-I |  | ON | #VALUE! | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33KV India habitat cen-II |  | 3.77 | 0.9425 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33kv vidut bhawan |  | 5.54 | 1.385 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV Scope Bldg.16 |  | 2.59 | 0.6475 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV NBCC |  | 1.66 | 0.415 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV Scope Bldg.15 |  | 2.22 | 0.555 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV Institutional Area |  | 1.85 | 0.4625 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV Defence colony Flyover |  | 3.51 | 0.8775 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV Lodhi Cly. |  | 0.92 | 0.23 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV NBCC East Block |  | 2.22 | 0.555 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV Defence Cly. |  | 2.03 | 0.5075 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
8 | 220KV SARITA VIHAR | 66KV MATHURA ROAD |  | 22 | 5.5 | Yes | No | yes | No | No | 48.8Hz | yes | yes | P143, Alstom Make | 20.06.15 | Ms Twinkle Gupta, Asstt. Manager
|  | 11KV S/STN-22 |  | 0.38104 | 0.09526 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV SARITA VIHAR -I |  | 2.4768 | 0.61919 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV ALLI VILLAGE |  | 3.8104 | 0.9526 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV JAIT PUR |  | 2.8578 | 0.71445 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV SARITA VHR-II |  | 4.382 | 1.0955 | Yes | No | yes | No | No | 49.0Hz | yes | yes
9 | 220KV GOPALPUR | 33KV AZADPUR-1 |  | 21.489 | 5.3723 | Yes | No | yes | No | No | 48.6Hz | yes | yes | P143, Alstom Make | 26.06.15 | Mr. Avishek Kumar Mallick, Asstt. Manager
|  | 33KV AZADPUR-2 |  | 21.489 | 5.3723 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV MUKHERGI NAGAR |  | 15 | 3.75 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV B.P.N COL0Y |  | 2.85 | 0.7125 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV SHAH ALAM BANDH |  | 3.306 | 0.8265 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV RAINY WELL |  | 5.453 | 1.3633 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV GANDHI VIHAR |  | 2.128 | 0.532 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV JAGATPUR |  | 3.211 | 0.80275 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
10 | 220KV SUBZIMANDI | 33KV O/G B.G.Rd. 1 |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 26.06.15 | Mr. Avishek Kumar Mallick, Asstt. Manager
|  | 33KV O/G B.G.Rd. 2 |  | 18.81 | 4.7025 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 33KV O/G Tripolia |  | 18.81 | 4.7025 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33 KVO/G Sahazada bagh-2 |  | 10.26 | 2.565 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 33KV O/G CVL. |  | 7.98 | 1.995 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33 KVO/G Gulabi bagh |  | 32.49 | 8.1225 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33 KV O/G D.U. |  | 7.98 | 1.995 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV Narbada cold storage |  | 0.855 | 0.21375 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV Subzi Mandi |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV Tilak Chowk |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV Bara Hindu Rao(P.S.) |  |  | 0 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV Prag Ice Fectory |  | 3.42 | 0.855 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV PALACE CINEMA |  | 3.705 | 0.92625 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11KV Kabir Basti |  | 2.185 | 0.54625 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
11 | 220KV NARAINA | 33KV Rewari line-I |  | 23.29 | 5.8225 | Yes | No | yes | No | No | 48.8Hz | yes | yes | P143, Alstom Make | 09.07.15 | Mr. VV Prasad, Asstt. Manager
|  | 33KV Payal |  | 23.29 | 5.8225 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11kv Gopi nath bazar |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11kv naraina |  | 3.42 | 0.855 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV A BLKshop. Complex |  | 2.24 | 0.56 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11kv Magoo-I |  | 2.68 | 0.67 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11kv Magoo-II |  | 1.94 | 0.485 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
12 | 220KV KANJHAWALA | 11KV Punjab Khera |  | 2.16 | 0.54 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 13.07.15 | Mohd. Ansar, Asstt. Manager
|  | 11kv O/H Rani khera |  | 3.9 | 0.975 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11kv ABC Kanjhawala |  | 3.6 | 0.9 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11kv S.O.S. Bawana |  | 0.07 | 0.0175 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV U/G Kanjhwala |  | 4.23 | 1.0575 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11kv O/H Kanjhawala |  | 3.57 | 0.8925 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11kV ABC Rani Kheda |  | 2.99 | 0.7475 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 11kv Ghewra |  | 3.2 | 0.8 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
13 | 220KV IP Station | 33kv Exhibition -I |  | 6.86 | 1.715 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 14.06.15 | Ms Twinkle Gupta, Asstt. Manager
|  | 33kv Exhibition -2 |  | 15.72 | 3.93 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV BAY-24 |  | 11.43 | 2.8575 | Yes | No | yes | No | No | 48.6Hz | yes | yes
14 | 220KV RPH | 33KV JAMA MASJID-1 |  | 7 | 1.75 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 26.06.15 | Ms. Ramneet Chanana, Asstt. Manager
|  | 33KV JAMA MASJID-2 |  | 7 | 1.75 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 33KV CIVIL LINE-1/GB Pant Hosp. |  | 7.4 | 1.85 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV LAHORI GATE-1 |  | 6.3 | 1.575 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV TOWN HALL-1 |  | 14.9 | 3.725 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 33KV TOWN HALL-2/ Minto Road |  | 7.9 | 1.975 | Yes | No | yes | No | No | 48.6Hz | yes | yes
15 | 220KV MASJID MOTH | 33KV BALAJI |  |  | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 24.06.15 | Mr Arpit Agarwal, Asstt. Manager
|  | 33KV PUSHPA VIHAR |  | 13.14 | 3.285 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33kV Alaknanda |  |  | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 33KV SHIVALIK |  | 31.44 | 7.86 | Yes | No | yes | No | No | 48.6Hz | yes | yes
16 | 220KV RIDGE VALLEY | 66kV Incomer-I |  | 50 | 35 | Yes | No | yes | No | No | 48.6Hz | yes | yes | P143, Alstom Make | 09.07.15 | Mr. VV Prasad, Asstt. Manager
17 | 220KV DIAL | 66KV DIAL-5 |  | 1 | 1 | Yes | No | yes | No | No | 48.6Hz | yes | yes | P143, Alstom Make | 10.07.15 | Mohd. Ansar, Asstt. Manager
|  | 66KV DIAL-6 |  | 1 | 1 | Yes | No | yes | No | No | 48.6Hz | yes | yes
18 | 400KV MUNDKA | 66KV GHEVRA |  | 35 | 8.75 | Yes | No | yes | No | No | 48.8Hz | yes | yes | P143, Alstom Make | 13.07.15 | Mohd. Ansar, Asstt. Manager
|  | 66KV MANGOLPURI |  | 49 | 12.25 | Yes | No | yes | No | No | 48.6Hz | yes | yes
19 | 220KV PPK-2 | 66KV G-15 DWARKA CKT-2 |  | 40.01 | 10.0025 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes | P143, Alstom Make | 10.07.15 | Mohd. Ansar, Asstt. Manager
|  | 66KV G-15 DWARKA CKT-1 |  | 43.44 | 10.86 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
20 | 220KV NARELA | 66KV BADLI-I |  | 33.26 | 8.315 | Yes | No | yes | No | No | 48.8Hz | yes | yes | P143, Alstom Make | 20.07.15 | Mohd. Ansar, Asstt. Manager
|  | 66KV BADLI-II |  | 33.26 | 8.315 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 66KV BHALASWA-I |  | 47.13 | 11.7825 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 66KV BHALASWA-II |  | 47.13 | 11.7825 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11kv U/G NARELA |  | 3.86 | 0.965 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV NARELA O/H |  | 3.47 | 0.8675 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV DDA-4 |  | 1 | 0.25 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11kv DDA-5 |  | 0.89 | 0.2225 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11kv DSIDC |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11kv BAWANA |  | 1.9 | 0.475 | Yes | No | yes | No | No | 49.0Hz | yes | yes
21 | 220KV SHALIMARHBAGH | 33KV RANI BAGH -1 |  | 12.2 | 3.05 | Yes | No | yes | No | No | 49.2Hz | yes | yes | P143, Alstom Make | 25.06.15 | Mr. Avishek Kumar Mallick, Asstt. Manager
|  | 33KV RANI BAGH -2 |  | 12.2 | 3.05 | Yes | No | yes | No | No | 49.2Hz | yes | yes
|  | 33KV SMB KHOSLA U/G-1 |  | 13.22 | 3.305 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 33KV SMB Facility Centre |  | 9.69 | 2.4225 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 33KV SMB KHOSLA O/H-2 |  | 25.37 | 6.3425 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33KV WAZIRPUR-1 |  | 22.57 | 5.6425 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33KV WAZIRPUR -2 |  | 19.04 | 4.76 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 11KV VILLAGE BADLI-2 |  | 2.052 | 0.513 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV 10- B SMB |  | 2.09 | 0.5225 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV KU PPR |  | 1.71 | 0.4275 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV 11-B SMB |  | 2.242 | 0.5605 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV FU S/Stn PPR |  | 3.173 | 0.79325 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
22 | 220KV ROHINI | 66KV Rohini-VI CKT-I |  | 0 | 0 | Yes | No | yes | No | No | 48.8Hz | yes | yes | P143, Alstom Make | 13.07.15 | Mohd. Ansar, Asstt. Manager
|  | 66KV Rohini-VI CKT-II |  | 0 | 0 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 66KV ROHINI -24 CKT.I |  | 29.94 | 7.485 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 66KV ROHINI -24 CKT.II |  | 29.94 | 7.485 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV O/H HYD. DISP. |  | 1.406 | 0.3515 | Yes | No | yes | No | No | 49.0Hz | yes | yes
23 | 220KV DSIDC BAWANA | 66KV NARELA-1 |  | 28 | 7 | Yes | No | yes | No | No | 48.6Hz | yes | yes | P143, Alstom Make | 20.07.15 | Mohd. Ansar, Asstt. Manager
|  | 66KV NARELA-2 |  | 28 | 7 | Yes | No | yes | No | No | 48.6Hz | yes | yes
24 | 220KV VASANT KUNJ | 66KV RIDGE VALLEY-I |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 23.06.15 | Mr Arpit Agarwal, Asstt. Manager
|  | 66KV RIDGE VALLEY-II |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66KV VASANT KUNJ C-I |  | 46.02 | 11.505 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 66KV VASANT KUNJ C-II |  | 47.13 | 11.7825 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV RANGPURI |  | 2.86 | 0.715 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV AB HOTEL |  | 1.39 | 0.3475 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV C9 VASANT KUNJ S/S 2 |  | 0.55 | 0.1375 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV C9 VASANT KUNJ S/S 5 |  | 0.92 | 0.23 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 11KV NANGAL DAIRY |  | 0.09 | 0.0225 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV C8 VASANT KUNJ S/S-I |  | 0.65 | 0.1625 | Yes | No | yes | No | No | 48.8Hz | yes | yes
25 | 220KV OKHLA | 66KV OKHLA-I |  | 44.35 | 11.0875 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 24.06.15 | Mr Arpit Agarwal, Asstt. Manager
|  | 66KV OKHLA-II |  | 44.35 | 11.0875 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66KV MALVIYA NGR-I |  | 24.39 | 6.0975 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 66KV MALVIYA NGR-II |  | 24.39 | 6.0975 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV OKHLA-I |  | 24.39 | 6.0975 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 33KV OKHLA-II |  | 16.08 | 4.02 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 33KV ALAKNANDA-I |  | 12.75 | 3.1875 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV BALAJI-I |  | 12.2 | 3.05 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33KV BALAJI-II |  | 11.64 | 2.91 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.1) | yes | yes
|  | 33KV MASJID MOTH |  | 12.75 | 3.1875 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33KV NEHRU PLACE-IV |  | 14.41 | 3.6025 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.2) | yes | yes
|  | 33KV NEHRU PLACE-I |  | 11.64 | 2.91 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 33KV NEHRU PLACE-II |  | 15.52 | 3.88 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 33KV TUGHLAKABAD |  | 24.39 | 6.0975 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
26 | 220KV MEHRAULI | 66KV VASANT KUNJ D-I |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes | P143, Alstom Make | 24.06.15 | Mr Arpit Agarwal, Asstt. Manager
|  | 66KV VASANT KUNJ D-II |  | 0 | 0 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66KV VASANT KUNJ C-I |  | 17.85 | 4.4625 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 66KV VASANT KUNJ C-II |  | 17.41 | 4.3525 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 66KV MALVIYA NAGAR-I |  | 41.91 | 10.4775 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 66KV MALVIYA NAGAR-II |  | 49.12 | 12.28 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV I/C NO. 1 |  | 6.28 | 1.57 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
|  | 11KV I/C NO. 2 |  | 7.2 | 1.8 | Yes | No | No | yes | No | Below 49.9 Hz (SLOPE 0.3) | yes | yes
27 | 220KV PARKSTREET | 33KV PRASAD NAGAR |  | 28.578 | 7.1445 | Yes | No | yes | No | No | 49.2Hz | yes | yes | P143, Alstom Make | 23.06.15 | Ms Twinkle Gupta, Asstt. Manager
|  | 66KV RIDGE VALLEY-1 |  | 25.1486 | 6.2872 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 66KV RIDGE VALLEY-2 |  | 18.8615 | 4.7154 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 33KV SHANKAR ROAD |  | 26.2918 | 6.5729 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 33KV MOTIA KHAN-1 |  | 0 | 0 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 33KV MOTIA KHAN-2 |  | 9.145 | 2.2862 | Yes | No | yes | No | No | 48.6Hz | yes | yes
28 | 220KV GAZIPUR | 66KV VIVEK VIHAR-I |  | 0 | 0 | Yes | No | yes | No | No | 48.8Hz | yes | yes | P143, Alstom Make | 15.06.15 | Ms Twinkle Gupta, Asstt. Manager
|  | 66KV VIVEK VIHAR-II |  | 53 | 13.25 | Yes | No | yes | No | No | 48.8Hz | yes | yes
|  | 66KV KONDLI-I |  | 36 | 9 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 66KV KONDLI-II |  | 34 | 8.5 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV FISH MKT.-II |  | 1.16 | 0.29 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV FISH MKT.-I |  | 0.24 | 0.06 | Yes | No | yes | No | No | 49.0Hz | yes | yes
|  | 11KV TELCO-I |  | 0 | 0 | Yes | No | yes | No | No | 48.6Hz | yes | yes
|  | 11KV TELCO-II |  | 0.15 | 0.0375 | Yes | No | yes | No | No | 48.6Hz | yes | yes
29 | 220kV Wazirpur | No tripping |  | NA | NA | NA | No | NA | NA | NA | NA | yes | yes | P143, Alstom Make | 13.07.15 | Ms. Ramneet Chanana, Asstt. Manager
29 | 220kV Peeragarhi | No tripping |  | NA | NA | NA | No | NA | NA | NA | NA | yes | yes | P143, Alstom Make | 13.07.15 | Ms. Ramneet Chanana, Asstt. Manager
30 | GTPS | No tripping |  | NA | NA | NA | No | NA | NA | NA | NA | yes | yes | P143, Alstom Make | 29.06.15 | Ms. Ramneet Chanana, Asstt. Manager
31 | 220kV AIIMS (Trauma Centre) | No tripping |  | NA | NA | NA | No | NA | NA | NA | NA | yes | yes | P143, Alstom Make | 23.06.15 | Mr. Arpit Agarwal, Asstt. Manager
32 | 220kV Electric Lane (HCML) | No tripping |  | NA | NA | NA | No | NA | NA | NA | NA | yes | yes | P143, Alstom Make | 19.06.15 | Mr. Arpit Agarwal, Asstt. Manager