DELHI TRANSCO LTD.

STATE LOAD DISPATCH CENTER

PROGRESS REPORT

*****************

MARCH - 2010

| S. No. | CONTENTS | Page No. |
| --- | --- | --- |
| 1. | Salient Features of Delhi Power System | 3 |
| 2. | Performance of Generating Stations within Delhi | 4 |
| 3. | Details of Outage of Generating Stations within Delhi | 5-24 |
| 4. | Allocation of Power to Delhi from unallocated quota of central sector | 25-26 |
| 5. | Allocation of Power to Discoms | 27 |
| 6. | Power Availability Demand Position of Delhi at the time of occurrence of Peak Demand | 28 |
| 7. | Power Availability Demand Position of Delhi at the time of occurrence of Maximum Un-Restricted Demand | 29 |
| 8. | Source wise scheduled drawl from grid and Availability within Delhi | 30-32 |
| 9. | Shedding Details | 33-36 |
| 10. | Load Curve for the Day of Peak Demand | 37 |
| 11. | Load Curve for the day of occurrence of Maximum Un-Restricted Demand | 38 |
| 12. | Load Curve for the day of Maximum Energy Consumed | 39 |
| 13. | Load Curve for the day of Maximum Un-Restricted Energy Demand | 40 |
| 14. | Load Duration Curve | 41 |
| 15. | Frequency Analysis | 42 |
| 16. | Voltage Profile for significant 220kV Sub-Stations | 43 |
| 17. | Voltage Profile for significant 400kV Sub-Stations | 44-45 |
| 18. | Details of Capacitors Installations in Delhi | 46-53 |
| 19. | Tripping Details of 400/220 KV System in Delhi Power System | 54-55 |
| 20. | Details of Under frequency Relay operations in Delhi Power System | 56-57 |

1	Salient Features of Delhi Power System

| Sr. No. | Features | MAR 2010 | MAR 2009 |
| --- | --- | --- | --- |
| 1 | Effective Generation Capacity within Delhi in MW |  |  |
|  | Indraprastha Power Station | NIL | 247.5 |
|  | Rajghat Power House | 135 | 135 |
|  | Gas Turbine | 270 | 282 |
|  | Pragati Power Corporation Ltd. | 330 | 330 |
|  | Badapur Thermal Power Station | 705 | 705 |
|  | Total | 1440 | 1699.5 |
| 2 | Maximum Unrestricted Demand (MW) | 3411 | 2999 |
|  | Date | 26.03.2010 | 19.03.2009 |
|  | Time | 19.20.11 | 19.21.10 |
| 3 | Peak Demand met (MW) | 3411 | 2999 |
|  | Date | 26.03.2010 | 19.03.2009 |
|  | Time | 19.20.11 | 19.21.00 |
| 4 | Peak Availability (MW) | 3410 | 2826 |
| 5 | Shortage (-) / Surplus (+) in MW | 1 | (-)173 |
| 6 | Percentage Shortage (-) / Surplus (+) | 0.03 | (-)5.77 |
| 7 | Maximum Energy Consume in a day (Mus) | 68.935 | 55.089 |
| 8 | Energy Consumed during the month | 1741.085 | 1549.698 |
| 9 | Load Shedding in Mus |  |  |
| A) | Due to Grid Restrictions |  |  |
| i) | Under Frequency Relay Operations | 0.276 | 0.085 |
| ii) | Manual Load shedding from DTL S/Stns. | 0.000 | 0.000 |
| iii) | Load Shedding due to low frequency / Low Voltage / TTC/ATC Violation |  |  |
|  | NDPL | 0.186 | 0.083 |
|  | BRPL | 0.468 | 0.240 |
|  | BYPL | 0.549 | 0.135 |
|  | NDMC | 0.000 | 0.000 |
|  | MES | 0.000 | 0.000 |
| iv) | Due to transmission Constraints in Central Sector | 1.203 | 0.000 |
|  | Total due to Grid Restriction | 1.479 | 0.543 |
| B) | Due to Constraints in System in Mus |  |  |
|  | DTL | 0.478 | 0.321 |
|  | NDPL | 3.775 | 0.411 |
|  | BRPL | 0.306 | 0.279 |
|  | BYPL | 0.311 | 0.068 |
|  | NDMC | 0.000 | 0.000 |
|  | MES | 0.000 | 0.000 |
|  | Other Agencies | 0.097 | 0.020 |
|  | Total | 4.967 | 1.099 |
| 11 | Grand Total in Mus | 6.446 | 1.642 |

2.	PERFORMANCE OF GENERATING STATIONS WITHIN DELHI DURING MAR. 2010

A)  For the month of March 2010

All Figures in MUs

| S. No | Stations | Gross Generation | Aux. Consumption | Net Generation | Availability (%) | Backing Down |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | IP | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 2. | RPH | 85.164 | 9.506 | 75.658 | 84.81 | 0.000 |
| 3. | GT | 117.470 | 4.471 | 112.999 | 63.77 | 7.25496 |
| 4. | PPCL | 230.136 | 5.822 | 224.314 | 93.83 | 1.41450 |
| 5. | BTPS | 366.71745 | 40.33892 | 326.37853 | 70.31 | 4.70250 |
|  | TOTAL | 799.48745 | 60.13792 | 739.34953 |  | 13.37196 |

B) For the Year 2009-10 (Upto March 2010)

| Power Station | Effective Capacity (MW) | Net Gene- ration in MUs For March 10 | Avail -ability (%) For Mar.’10 | PLF (%) For Mar. 10 | Cumulative Generation in MUs upto Mar 10 for the year 2009-10 | Cumulative Availability in % upto Mar. 10 for the year 2009-10 | Cumulative PLF in % upto Mar 10 for the year 2009-10 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| IP | 247.5 | 0.000 | 0.000 |  | 386.166 | -- |  |
| RPH | 135 | 75.658 | 84.81 | 84.81 | 554.370 | 54.64 | 54.64 |
| GT | 282 | 112.999 | 63.77 | 60.05 | 1446.079 | 73.28 | 63.21 |
| PPCL | 330 | 224.314 | 93.83 | 93.24 | 2385.985 | 85.50 | 84.24 |
| BTPS | 705 | 326.37853 | 70.31 | 69.31 | 4701.352 | 86.46 | 84.24 |
| TOTAL | 1699.5 | 739.34953 |  |  | 9473.952 |  |  |

3	DETAILS OF OUTAGES OF GENERATING STNS. WITHIN DELHI W.E.F. APRIL 2009

(A)  IP STATION

| Unit no. | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 2 | 62.5 | 03.04.09 | 07.02 | 03.04.09 | 08.58 | D- Rediator Level not maintained. |
|  |  | 03.04.09 | 09.35 | 05.04.09 | 07.25 | Loss of excitation |
|  |  | 21.04.09 | 05.22 | 27.04.09 | 23.05 | Boiler Tube Leakage |
|  |  | 17.05.09 | 00.07 | 19.05.09 | 12.03 | Problem in Bottom System |
|  |  | 19.05.09 | 21.20 | 20.05.09 | 02.15 | Low vacuum |
|  |  | 22.05.09 | 14.39 | 22.05.09 | 16.15 | Due to tripping of associated transmission lines. |
|  |  | 01.06.09 | 09.25 | 01.06.09 | 11.08 |  |
|  |  | 05.06.09 | 15.08 | 05.06.09 | 16.40 |  |
|  |  | 15.06.09 | 13.32 | 15.06.9 | 14.30 |  |
|  |  | 29.06.09 | 22.50 | 01.07.09 | 15.45 | Boiler Tube Leakage |
|  |  | 06.07.09 | 12.40 | 06.07.09 | 13.53 | Fire out. |
|  |  | 14.07.09 | 09.40 | 14.07.09 | 11.35 | Due to tripping of associated transmission lines. |
|  |  | 28.07.09 | 10.53 | 28.07.09 | 20.15 | Steam line burnt |
|  |  | 03.08.09 | 05.05 | 03.08.09 | 17.52 | Problem in Boiler Feed Pump |
|  |  | 11.08.09 | 17.50 | 13.08.09 | 07.40 | Boiler Tube Leakage |
|  |  | 27.08.09 | 17.30 | 08.09.09 | 20.28 | Due to tripping of associated transmission lines. Could not synchronized due to Durator Valve Knob |
|  |  | 11.09.09 | 07.55 | 11.09.09 | 14.42 | CHP Problem |
|  |  | 12.09.09 | 11.25 | 15.09.09 | 07.58 | Boiler Tube Leakage |
|  |  | 26.09.09 | 21.45 | 29.09.09 | 17.52 | Steam Leakage in Turbine |
|  |  | 29.09.09 | 20.15 | 30.09.09 | 08.18 | Generator Stator Temp High |
|  |  | 08.10.09 | 18.18 | 11.10.09 | 13.42 | Boiler Tube Leakage |
|  |  | 26.10.09 | 09.25 | 26.10.09 | 21.40 | No Coal flow |
|  |  | 27.10.09 | 05.58 | 27.10.09 | 09.10 | No Coal flow |
|  |  | 31.10.09 | 21.40 |  |  | Unit stopped |
| 3 | 62.5 | 06.04.09 | 13.38 | 09.04.09 | 07.07 | Boiler Tube Leakage |
|  |  | 06.05.09 | 06.30 | 08.05.09 | 21.55 | Boiler Tube Leakage |
|  |  | 19.05.09 | 21.11 | 20.05.09 | 04.58 | Low vacuum |
|  |  | 28.05.09 | 09.22 | 28.05.09 | 11.35 | Bus differential operation. |
|  |  | 01.06.09 | 09.29 | 01.06.09 | 11.52 | Due to tripping of associated transmission lines. |
|  |  | 10.06.09 | 09.52 | 10.06.09 | 12.10 | Vacuum Problem |
|  |  | 14.06.09 | 00.01 | 28.06.09 | 08.35 | Boiler Tube Leakage |
|  |  | 12.07.09 | 10.50 | 15.07.09 | 00.12 | Boiler Tube Leakage |
|  |  | 31.07.09 | 20.30 | 01.08.09 | 04.44 | Due to jerk |
|  |  | 02.08.09 | 22.58 | 03.08.09 | 10.30 | Low coal flow |
|  |  | 05.08.09 | 00.10 | 08.08.09 | 01.50 | Condenser Tube Leakage |
|  |  | 11.08.09 | 09.30 | 11.08.09 | 15.43 | No Coal Flow |
|  |  | 17.08.09 | 08.55 | 17.08.09 | 11.43 | Due to tripping of associated transmission lines. |
|  |  | 17.08.09 | 14.01 | 18.08.09 | 23.55 | Problem in Coal Bunker |
|  |  | 24.08.09 | 21.10 | 25.08.09 | 20.25 | Shortage of DM Water. |
|  |  | 27.08.09 | 17.50 | 28.08.09 | 00.50 | Due to tripping of associated transmission lines. |
|  |  | 28.08.09 | 22.50 | 06.09.09 | 14.02 | Boiler Tube Leakage |
|  |  | 08.09.09 | 23.40 | 09.09.09 | 20.20 | Condenser Tube Leakage |
|  |  | 24.09.09 | 12.15 | 27.09.09 | 07.30 | ID Fan problem |
|  |  | 04.10.09 | 09.35 | 05.10.09 | 09.50 | Leakage in Control Valve Pipe |
|  |  | 20.10.09 | 23.55 | 23.10.09 | 07.20 | Coal Mill Problem |
|  |  | 28.10.09 | 21.30 |  |  | Unit stopped |

| Unit no. | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 4 | 62.5 | 04.04.09 | 10.30 | 04.04.09 | 12.32 | Electrocution Trip Device Alarm |
|  |  | 29.04.09 | 05.10 | 29.04.09 | 09.35 | Coal mill problem |
|  |  | 29.04.09 | 12.43 | 13.05.09 | 16.43 | Main Buchloz Relay Operated(Tx-4) |
|  |  | 19.05.09 | 21.11 | 24.05.09 | 15.05 | Low vacuum |
|  |  | 25.05.09 | 19.42 | 27.05.09 | 23.15 | Boiler Tube Leakage |
|  |  | 28.05.09 | 09.25 | 28.05.09 | 10.34 | Bus differential operation. |
|  |  | 01.06.09 | 09.25 | 12.06 | 18.45 | Reduction Gear Problem |
|  |  | 15.06.09 | 13.32 | 15.06.09 | 15.10 | Due to tripping of associated transmission lines. |
|  |  | 22.06.09 | 20.57 | 24.06.09 | 04.40 | Boiler Tube Leakage |
|  |  | 29.06.09 | 22.50 | 30.06.09 | 01.40 | Due to tripping of associated transmission lines. |
|  |  | 04.07.09 | 06.00 | 15.07.09 | 16.25 | Shortage of DM water |
|  |  | 26.07.09 | 15.55 | 27.07.09 | 07.12 | Due to fire in boiler |
|  |  | 28.07.09 | 05.30 | 30.07.09 | 01.10 | Shortage of coal |
|  |  | 03.08.09 | 07.30 | 03.08.09 | 08.58 | Low Vacuum |
|  |  | 10.08.09 | 04.25 | 10.08.09 | 22.55 | Coal Bunker Empty |
|  |  | 17.08.09 | 08.55 | 17.08.09 | 10.05 | Coal Bunker Empty |
|  |  | 18.08.09 | 05.40 | 18.05.09 | 06.58 | Low Coal Flow |
|  |  | 18.08.09 | 07.10 | 28.08.09 | 11.55 | Condenser Tube Leakage |
|  |  | 28.08.09 | 14.45 | 29.08.09 | 13.12 | Heavy Steam Leakage in Boiler |
|  |  | 04.09.09 | 01.55 | 04.09.09 | 11.32 | Tripped on ETD |
|  |  | 04.09.09 | 14.40 | 06.09.09 | 04.45 | Boiler Tube Leakage |
|  |  | 12.09.09 | 16.37 | 12.09.09 | 20.55 | Fire out |
|  |  | 17.09.09 | 19.45 | 19.09.09 | 23.55 | Boiler Tube Leakage |
|  |  | 03.10.09 | 18.27 | 17.10.09 | 05.30 | Boiler Tube Leakage |
|  |  | 20.10.09 | 07.25 | 20.10.09 | 07.20 | Coal mill problem |
|  |  | 20.10.09 | 23.55 | 23.10.09 | 15.16 | Coal mill problem |
|  |  | 26.10.09 | 15.35 | 28.10.09 | 21.40 | No coal availability |
|  |  | 29.10.09 | 18.22 | 29.10.09 | 22.50 | No coal availability |
|  |  | 29.10.09 | 23.07 | 30.10.09 | 00.10 | Heat Control valve leakage |
|  |  | 01.11.09 | 00.10 | 01.11.09 | 10.35 | No coal availability |
|  |  | 02.11.09 | 13.47 | 02.11.09 | 17.18 | Water level low |
|  |  | 03.11.09 | 10.15 | 04.11.09 | 17.34 | No coal availability |
|  |  | 05.11.09 | 03.58 | 05.11.09 | 05.00 | No coal availability |
|  |  | 05.11.09 | 09.12 | 05.11.09 | 18.18 | No coal availability |
|  |  | 05.11.09 | 16.28 | 09.11.09 | 15.20 | No coal availability |
|  |  | 10.11.09 | 21.40 | 24.11.09 | 13.40 | Boiler Tube Leakage |
|  |  | 24.11.09 | 13.50 | 26.11.09 | 14.00 | Boiler Tube Leakage |
|  |  | 27.11.09 | 18.10 | 27.11.09 | 20.45 | No coal availability |
|  |  | 28.11.09 | 13.55 | 28.11.09 | 16.55 | No coal availability |
| 5 | 60 | 31.03.09 | 04.03 | 04.04.09 | 05.58 | Electrocution Trip Device Alarm |
|  |  | 09.04.09 | 02.40 | 12.04.09 | 00.35 | Boiler Tube Leakage |
|  |  | 12.04.09 | 17.40 | 15.04.09 | 16.45 | Electrocution Trip Device Alarm |
|  |  | 15.04.09 | 19.43 | 18.04.09 | 23.17 | Electrocution Trip Device Alarm |
|  |  | 22.04.09 | 19.02 | 24.04.09 | 16.00 | Condenser Tube Leakage |
|  |  | 04.05.09 | 09.45 | 04.05.09 | 10.26 | Tripped due to jerk due to tripping of 33kV Bay-29 |
|  |  | 04.05.09 | 20.56 | 11.05.09 | 05.15 | Fire in PA Fan |
|  |  | 15.05.09 | 23.18 | 16.05.09 | 07.40 | Problem in RC Feeder |

| Unit no. | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 5 | 60 | 18.05.09 | 13.10 | 05.07.09 | 03.45 | ID Fan Problem |
|  |  | 05.07.09 | 07.00 | 08.07.09 | 02.35 | Boiler Tube Leakage |
|  |  | 08.07.09 | 10.30 | 12.07.09 | 03.24 | Condenser Tube Leakage |
|  |  | 13.07.09 | 06.50 | 13.07.09 | 07.05 | Drum level high |
|  |  | 13.07.09 | 07.50 | 13.07.09 | 23.25 | Shortage of DM water |
|  |  | 14.07.09 | 09.42 | 14.07.09 | 18.55 | Due to tripping of associated transmission lines |
|  |  | 26.07.09 | 16.02 | 28.07.09 | 20.05 | Condenser Tube Leakage |
|  |  | 29.07.09 | 12.12. | 29.07.09 | 12.55 | Auxiliary supply failure |
|  |  | 31.07.09 | 07.35 | 31.07.09 | 08.35 | Fire out |
|  |  | 06.08.09 | 20.48 | 11.08.09 | 08.30 | Condenser Tube Leakage |
|  |  | 11.08.09 | 08.35 | 11.08.09 | 09.08 | Low Vacuum |
|  |  | 15.08.09 | 05.02 | 15.08.09 | 17.10 | Maintenance work |
|  |  | 17.08.09 | 11.28 | 19.08.09 | 18.50 | Problem in coal bunker |
|  |  | 21.08.09 | 13.27 | 21.08.09 | 13.55 | Tripped due to jerk |
|  |  | 23.08.09 | 21.01 | 29.08.09 | 22.50 | Shortage of DM Water |
|  |  | 03.09.09 | 17.46 | 09.09.09 | 07.52 | Vapour Fan5-1 & Mill 5-2 out |
|  |  | 09.09.09 | 13.40 | 13.09.09 | 13.15 | Low vacuum |
|  |  | 17.09.09 | 12.45 | 17.09.09 | 18.25 | Low vacuum |
|  |  | 19.09.09 | 18.22 | 19.09.09 | 19.20 | Low vacuum |
|  |  | 20.09.09 | 12.42 | 27.09.09 | 12.47 | Coal Mill Problem |
|  |  | 28.09.09 | 02.50 | 03.10.09 | 03.05 | Boiler Tube Leakage |
|  |  | 03.10.09 | 18.09 | 31.10.09 | 18.50 | Due to tripping of 33kV Bay-38 |
|  |  | 04.10.09 | 22.58 | 12.10.09 | 13.55 | Boiler Tube Leakage |
|  |  | 14.10.09 | 20.00 | 16.10.00 | 14.20 | Boiler Tube Leakage |
|  |  | 17.10.09 | 21.55 | 18.10.09 | 06.35 | Coal not available |
|  |  | 22.10.09 | 09.45 | 01.11.09 | 03.20 | Boiler Tube Leakage |
|  |  | 02.11.09 | 17.40 | 23.11.09 | 16.10 | No coal availability |
|  |  | 24.11.09 | 02.05 |  |  | Unit stopped |

(B)  	RPH STATION

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 67.5 | 05.04.09 | 07.05 | 05.04.09 | 08.05 | Bus Bar Protection Operated |
|  |  | 10.04.09 | 08.48 | 10.04.09 | 19.33 | Condenser Tube Leakage |
|  |  | 09.05.09 | 03.16 | 09.05.09 | 09.46 | Cooling Line Problem |
|  |  | 12.05.09 | 20.05 | 13.05.09 | 14.26 | Turbine Vibration High |
|  |  | 22.05.09 | 14.39 | 22.05.09 | 10.02 | Tripped due to tripping of associated transmission lines |
|  |  | 01.06.09 | 09.24 | 01.06.09 | 10.35 |  |
|  |  | 05.06.09 | 15.10 | 05.06.09 | 17.16 |  |
|  |  | 15.06.09 | 13.35 | 15.06.09 | 15.20 |  |
|  |  | 29.06.09 | 15.40 | 29.06.09 | 20.50 |  |
|  |  | 03.07.09 | 01.20 | 06.07.09 | 14.20 | Thrust bearing maintenance. |
|  |  | 06.07.09 | 23.33 | 07.07.09 | 15.22 | Condenser Vacuum low |
|  |  | 07.07.09 | 20.09 | 07.07.09 | 20.42 | Flam failure |
|  |  | 14.07.09 | 09.42 | 14.07.09 | 14.48 | Tripped due to tripping of associated transmission lines |
|  |  | 15.07.09 | 22.30 | 18.07.09 | 11.05 | Condenser Tube Leakage |
|  |  | 18.07.09 | 11.20 | 18.07.09 | 12.05 | Boiler Flame Failure |
|  |  | 28.07.09 | 15.27 | 28.07.09 | 16.22 | Flame Failure |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 67.5 | 28.07.09 | 18.03 | 28.07.09 | 18.39 | Flame Failure |
|  |  | 30.07.09 | 10.52 | 31.07.09 | 11.40 | Condenser Tube Leakage |
|  |  | 31.07.09 | 12.32 | 31.07.09 | 13.15 | Drum level high |
|  |  | 01.08.09 | 07.52 | 01.08.09 | 08.55 | Jerk due to appearance of money in yard |
|  |  | 01.08.09 | 18.20 | 01.08.09 | 19.01 | Flame failure |
|  |  | 02.08.09 | 15.19 | 02.08.09 | 15.45 | Flame failure |
|  |  | 07.08.09 | 10.44 | 07.08.09 | 11..31 | Flame failure |
|  |  | 09.08.09 | 03.55 | 09.08.09 | 04.25 | Flame failure |
|  |  | 21.08.09 | 14.34 | 21.08.09 | 18.00 | Buchloz Relay operated |
|  |  | 23.08.09 | 19.31 | 23.08.09 | 20.07 | Burner Pressure High |
|  |  | 25.08.09 | 17.50 | 25.08.09 | 18.25 | High Furnace pressure. |
|  |  | 27.08.09 | 17.35 | 27.08.09 | 20.30 | Boiler flame failure |
|  |  | 01.09.09 | 05.26 | 01.09.09 | 06.18 | Flame failure |
|  |  | 01.09.09 | 10.17 | 02.09.09 | 11.48 | Tripped due to tripping of associated transmission lines |
|  |  | 06.09.09 | 18.35 | 06.09.09 | 18.58 | Flame failure |
|  |  | 11.09.09 | 04.38 | 11.09.09 | 05.05 | Flame failure |
|  |  | 11.09.09 | 23.50 | 13.09.09 | 18.08 | Boiler Tube Leakage |
|  |  | 13.09.09 | 19.51 | 13.09.09 | 22.32 | Unit Auxiliary TX. tripped on E/F |
|  |  | 14.09.09 | 06.58 | 14.09.09 | 07.50 | Flame failure |
|  |  | 16.09.09 | 05.24 | 16.09.09 | 05.59 | Flame failure |
|  |  | 02.10.09 | 09.43 | 03.10.09 | 10.09 | To attend various leakages |
|  |  | 03.10.09 | 10.58 | 03.10.09 | 11.14 | Flame failure |
|  |  | 10.10.09 | 17.03 | 11.10.09 | 02.35 | To attend raw water |
|  |  | 02.11.09 | 22.24 | 02.11.09 | 23.01 | Control supply fail |
|  |  | 11.11.09 | 20.00 | 13.11.09 | 13.58 | Condenser Tube Leakage |
|  |  | 25.11.09 | 21.30 | 25.11.09 | 23.00 | To attend diesel generator set |
|  |  | 04.12.09 | 09.30 | 04.12.09 | 10.07 | Flame failure |
|  |  | 09.12.09 | 16.23 | 09.12.09 | 17.23 | Turbine Trip |
|  |  | 10.12.09 | 02.25 | 10.12.09 | 02.50 | Turbine Trip |
|  |  | 10.12.09 | 08.35 | 12.12.09 | 00.46 | Boiler Tube Leakage |
|  |  | 16.12.09 | 10.16 | 16.12.09 | 11.23 | Turbine Trip |
|  |  | 23.12.09 | 04.50 | 23.12.09 | 13.56 | Turbine Trip |
|  |  | 26.12.09 | 10.45 | 26.12.09 | 11.45 | Drum level low |
|  |  | 29.12.09 | 13.16 | 29.12.09 | 14.35 | Drum level low. |
|  |  | 02.01.10 | 04.18 | 03.01.10 | 00.35 | Due to tripping of transmission lines in Northern Region due to fog |
|  |  | 03.01.10 | 01.35 | 03.01.10 | 20.00 | Flame failure |
|  |  | 04.01.10 | 14.12 | 10.01.10 | 21.57 | Due to shut-down of 220kV IP – RPH Ckt-I & II |
|  |  | 11.01.10 | 15.58 | 14.01.10 | 00.23 | Due to tripping of transmission lines. Later taken on shut-down |
|  |  | 25.01.10 | 08.21 | 25.01.10 | 08.50 | Boiler tripped |
|  |  | 29.01.10 | 02.54 | 29.01.10 | 16.34 | Boiler drum level high |
|  |  | 31.01.10 | 16.28 | 31.01.10 | 17.23 | Tripped due to jerk |
|  |  | 03.02.10 | 21.13 | 0302.10 | 21.43 | Electrical Problem |
|  |  | 06.02.10 | 10.38 | 06.02.10 | 12.16 | Tripped along with tripping of associated transmission lines |
|  |  | 06.02.10 | 16.44 | 06.02.10 | 17.57 | Electrical fault |
|  |  | 09.02.10 | 08.14 | 09.02.10 | 08.35 | Boiler Flame Failure |
|  |  | 10.02.10 | 12.45 | 10.02.10 | 16.44 | Due to jerk |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 67.5 | 12.02.10 | 17.28 | 12.02.10 | 18.47 | Electrical problem |
|  |  | 13.02.10 | 06.22 | 14.02.10 | 06.50 | Flame failure |
|  |  | 14.02.10 | 17.37 | 14.02.10 | 18.45 | Tripped along with tripping of associated transmission lines |
|  |  | 19.02.10 | 17.05 | 19.02.10 | 17.23 | Cooling pump tripped |
|  |  | 20.02.10 | 06.32 | 22.02.10 | 22.25 | Maintenance work of cooling line |
|  |  | 07.03.10 | 17.54 | 07.03.10 | 18.30 | Electric supply failed |
|  |  | 21.03.10 | 26.00 | 21.03.10 | 17.45 | 33kV Bus differential operation |
|  |  | 23.03.10 | 10.28 | 23.03.10 | 11.54 | Electrical Trouble |
|  |  | 24.03.10 | 03.10 | 24.03.10 | 21.12 | Low vacuum |
|  |  | 27.03.10 | 14.01 | 27.03.10 | 15.14 | Tripped along with tripping of associated transmission lines. |
| 2 | 67.5 | 05.04.09 | 07.05 | 05.04.09 | 08.05 | Bus Bar Protection Operated |
|  |  | 09.04.09 | 02.26 | 09.04.09 | 23.20 | Boiler Tube Leakage |
|  |  | 25.04.09 | 19.30 | 25.04.09 | 21.52 | Shaft Vibration High |
|  |  | 08.05.09 | 08.54 | 09.05.09 | 10.05 | Condenser Tube Leakage |
|  |  | 11.05.09 | 20.49 | 11.05.09 | 22.10 | Turbine Vibration high |
|  |  | 20.05.09 | 10.04 | 20.05.09 | 12.05 | Turbine Vibration high |
|  |  | 22.05.09 | 14.39 | 23.05.09 | 00.41 | Tripped due to tripping of associated transmission lines |
|  |  | 01.06.09 | 09.24 | 01.06.09 | 11.10 |  |
|  |  | 01.06.09 | 11.42 | 01.06.09 | 13.20 | Low vacuum |
|  |  | 05.06.09 | 15.10 | 05.06.09 | 17.45 | Tripped due to tripping of associated transmission lines |
|  |  | 07.06.09 | 07.25 | 07.06.09 | 21.06 | To check Turbine in Auxiliary |
|  |  | 15.06.09 | 13.35 | 15.06.09 | 15.27 | Tripped due to tripping of associated transmission lines |
|  |  | 06.07.09 | 23.34 | 07.07.09 | 15.20 | Condenser Vacuum low |
|  |  | 10.07.09 | 22.08 | 10.07.09 | 23.08 | Condenser Vacuum low |
|  |  | 14.07.09 | 09.42 | 14.07.09 | 15.20 | Tripped due to tripping of associated transmission lines |
|  |  | 18.07.09 | 20.20 | 19.07.09 | 11.45 | Electrical Fault |
|  |  | 01.08.09 | 01.15 | 03.08.09 | 05.58 | Condenser Tube Leakage |
|  |  | 21.08.09 | 16.28 | 21.08.09 | 18.54 | Furnace Pressure High |
|  |  | 27.08.09 | 17.51 | 27.08.9 | 22.08 | Tripped due to tripping of associated transmission lines |
|  |  | 28.08.09 | 00.18 | 28.08.09 | 01.33 | Turbine Tripped |
|  |  | 28.08.09 | 03.16 | 28.08.09 | 04.33 | Turbine Tripped |
|  |  | 28.08.09 | 03.57 | 29.08.09 | 04.15 | Turbine Tripped |
|  |  | 29.08.09 | 12.25 | 30.08.09 | 00.38 | Condenser Tube Leakage |
|  |  | 31.08.09 | 18.03 | 31.08.09 | 19.07 | Low Vacuum |
|  |  | 02.09.09 | 10.17 | 02.09.09 | 11.52 | Tripped due to tripping of associated transmission lines |
|  |  | 10.09.09 | 08.23 | 10.09.09 | 17.20 | Stator Earth Fault |
|  |  | 12.09.09 | 16.10 | 30.11.09 | 08.24 | For major overhauling |
|  |  | 30.11.09 | 14.36 | 30.11.09 | 19.41 | Shaft vibration high |
|  |  | 01.12.09 | 00.08 | 01.12.09 | 04.20 | Turbine problem |
|  |  | 01.12.09 | 21.14 | 01.12.09 | 22.56 | Drum level low |
|  |  | 05.12.09 | 15.30 | 05.12.09 | 17.59 | Turbine failure |
|  |  | 06.12.09 | 18.35 | 06.12.09 | 20.05 | Turbine failure |
|  |  | 11.12.09 | 06.24 | 11.12.09 | 07.26 | Turbine failure |
|  |  | 14.12.09 | 15.52 | 18.12.09 | 15.07 | Boiler Tube Leakage |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 2 | 67.5 | 18.12.09 | 21.05 | 22.12.09 | 20.32 | Boiler Tube Leakage |
|  |  | 02.01.10 | 04.18 | 04.01.10 | 20.00 | Due to tripping of transmission lines in Northern Region due to fog |
|  |  | 04.01.10 | 14.12 | 11.01.10 | 02.00 | Due to Shut-down of 220kV IP – RPH Ckt-I & II |
|  |  | 11.01.10 | 15.58 | 11.01.10 | 17.35 | Tripped due to tripping of associated transmission lines |
|  |  | 11.01.10 | 18.04 | 28.02.10 | 11.35 | Turbine Vibration high |
|  |  | 07.03.10 | 17.54 | 07.03.10 | 19.58 | Electrical supply failed |
|  |  | 21.03.10 | 16.00 | 21.03.10 | 17.45 | 33kV bus differential operation |
|  |  | 23.03.10 | 10.28 | 23.03.10 | 12.12 | Electrical trouble |
|  |  | 30.03.10 | 18.46 | 30.03.10 | 20.30 | Drum level low |

(C)	Gas Turbine

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 30 | 15.04.09 | 16.15 | 16.04.09 | 22.55 | Due to overloading on 100 MVA Tr |
|  |  | 05.05.09 | 08.01 | 05.05.09 | 13.00 |  |
|  |  | 05.05.09 | 13.00 | 05.05.09 | 19.45 | For installing the ABT Meter. |
|  |  | 12.06.09 | 15.15 | 12.06.09 | 15.44 | FSNL due to tripping of 160 MVA Tx at both end |
|  |  | 28.06.09 | 06.02 | 29.06.9 | 00.28 | To attend HSD leakag from the Nozzles. |
|  |  | 08.07.09 | 23.54 | 09.07.09 | 02.07 | Due to combined cycle trip alarm. |
|  |  | 09.07.09 | 11.40 | 17.07.09 | 08.55 | To attend the GT duct for HRSG# 1. |
|  |  | 17.07.09 | 13.16 | 17.07.09 | 16.14 | Emergency manual trip alarm |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 07.20 | Tripped due to blast in the breaker of 5 MVA in switch gear room.. |
|  |  | 21.08.09 | 16.49 | 21.08.09 | 18.11 | SF6 gas pressure low |
|  |  | 23.08.09 | 06.05 | 23.08.09 | 21.10 | Gas Restriction |
|  |  | 28.08.09 | 04.32 | 28.08.09 | 05.45 | Exhaust Temperature High |
|  |  | 01.09.09 | 22.35 | 02.09.09 | 03.25 | Electrical Problem |
|  |  | 13.09.09 | 11.35 | 13.09.09 | 18.25 | To charge 66KV Dead Bus from Grid. |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 16.50 | Tripped due to Grid failure. |
|  |  | 17.09.09 | 19.40 | 17.09.09 | 22.55 | Gas restriction |
|  |  | 20.09.09 | 06.02 | 20.09.09 | 09.45 | Gas restriction |
|  |  | 23.09.09 | 06.27 | 23.09.09 | 08.02 | Loss of flame. |
|  |  | 23.09.09 | 16.15 | 24.09.09 | 00.05 | To repair liquid fuel pump |
|  |  | 24.09.09 | 11.30 | 24.09.09 | 20.10 | To replace liquid fuel pump. |
|  |  | 26.09.09 | 08.05 | 26.09.09 | 08.10 | Came on FSNL due to jerk |
|  |  | 26.09.09 | 22.15 | 26.09.09 | 23.13 | High Exhaust Temperature |
|  |  | 30.09.09 | 11.47 | 30.09.09 | 13.55 | Tripped on gen. over current alarm |
|  |  | 09.10.09 | 22.40 | 10.10.09 | 02.50 | Generator O/C, Over voltage alarm appeared on protection panel. |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 15.30 | Tripped due to Grid Failure |
|  |  | 04.11.09 | 19.50 | 04.11.09 | 20.28 | Failure of supply to HSD pump. |
|  |  | 17.11.09 | 14.15 | 18.11.09 | 17.58 | Gas restriction |
|  |  | 01.12.09 | 18.15 | 10.12.09 | 14.15 | Available on liquid fuel |
|  |  | 11.12.09 | 13.37 | 11.12.09 | 14.15 | Tripped on high TAD |
|  |  | 11.01.10 | 23.02 | 12.01.10 | 07.00 | Sswapping of gas to PPCL |
|  |  | 12.01.10 | 07.00 | 12.01.10 | 16.45 | Problem in DG set |
|  |  | 12.01.10 | 17.17 | 20.01.10 | 18.31 | Tripped on high Exhaust temperature |
|  |  | 21.01.10 | 07.35 | 21.01.10 | 08.27 | Tripped on loss of flame |
|  |  | 22.01.10 | 16.12 | 22.01.10 | 17.19 | Came on FSNL due to tripping of 160 MVA Transformer |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 30 | 31.01.10 | 09.05 | 01.02.10 | 04.05 | Available on Open Cycle |
|  |  | 05.02.10 | 15.55 | 05.02.10 | 16.44 | Due to tripping of 100MVA & 160MVA Tx on jerk |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 14.48 | Bus Bar differential operation |
|  |  | 13.03.10 | 08.07 | 22.03.10 | 07.16 | Tripped on Reverse power alarm |
|  |  | 24.03.10 | 06.40 | 24.03.10 | 09.15 | Control supply fuse failure. |
|  |  | 29.03.10 | 02.48 | 29.03.10 | 20.45 | Tripping of 160 MVA TX. at GT end. |
| 2 | 30 | 02.04.09 | 12.47 | 03.04.09 | 05.55 | Gas Restriction |
|  |  | 08.04.09 | 12.02 | 30.04.09 | 24.00 | Major Overhauling |
|  |  | 01.05.09 | 00.00 | 19.05.09 | 13.35 | Stopped for Major Inspection. |
|  |  | 22.05.09 | 20.10 | 23.05.09 | 21.50 | Swapping of gas to PPCL |
|  |  | 24.05.09 | 11.05 | 26.05.09 | 14.20 | Available on Open Cycle |
|  |  | 28.05.09 | 01.05 | 28.05.09 | 11.38 | Gas Restriction |
|  |  | 28.05.09 | 12.00 | 28.05.09 | 13.14 | Gas Restriction |
|  |  | 30.0.09 | 12.55 | 30.05.09 | 19.58 | Gas Restriction |
|  |  | 30.05.09 | 22.32 | 31.05.09 | 23.59 | Gas Restriction |
|  |  | 01.06.09 | 00.00 | 01.06.09 | 19.42 | Gas Restriction |
|  |  | 03.06.09 | 05.50 | 03.06.09 | 17.14 | Gas Restriction |
|  |  | 04.06.09 | 06.32 | 04.06.09 | 09.35 | Gas Restriction |
|  |  | 05.06.09 | 11.30 | 05.06.09 | 19.35 | Gas Restriction |
|  |  | 07.06.09 | 01.48 | 07.06.09 | 18.45 | Gas Restriction |
|  |  | 08.06.09 | 00.10 | 08.06.09 | 18.20 | To attending Leakages |
|  |  | 09.06.09 | 00.02 | 09.06.09 | 10.35 | To attending Leakages |
|  |  | 10.06.09 | 07.09 | 10.06.09 | 17.50 | To attending Leakages |
|  |  | 11.06.09 | 07.47 | 11.06.09 | 19.55 | To attending Leakages |
|  |  | 12.06.09 | 03.02 | 15.06.09 | 19.20 | Swapping of gas to PPCL |
|  |  | 16.06.09 | 06.02 | 16.06.09 | 15.25 | Swapping of gas to PPCL |
|  |  | 16.06.09 | 15.55 | 16.06.09 | 20.45 | Exhaust Temperature high |
|  |  | 16.06.09 | 20.45 | 17.06.09 | 01.20 | Gas Restriction |
|  |  | 17.06.09 | 01.32 | 17.06.09 | 10.27 | Exhaust Temperature high |
|  |  | 17.06.09 | 11.30 | 17.06.09 | 14.32 | Gas Restriction |
|  |  | 18.06.09 | 00.02 | 21.06.09 | 11.20 | Swapping of gas to PPCL |
|  |  | 24.06.09 | 00.32 | 25.06.09 | 09.50 | Swapping of gas to PPCL |
|  |  | 26.06.09 | 22.25 | 26.06.09 | 22.55 | Exhaust Temperature high |
|  |  | 30.06.09 | 20.20 | 02.07 | 14.05 | Gas Restriction |
|  |  | 02.07.09 | 18.32 | 03.07.09 | 03.15 | Gas Restriction |
|  |  | 03.07.09 | 18.02 | 03.07.09 | 23.50 | Gas Restriction |
|  |  | 04.07.09 | 01.05 | 04.07.09 | 16.10 | Gas Restriction |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 06.38 | Due to blast in the breaker of 5 MVA in switch gear room. |
|  |  | 22.07.09 | 04.04 | 23.07.09 | 13.20 | To attend lube oil leakages. |
|  |  | 04.08.09 | 07.25 | 04.08.09 | 08.13 | Tripped while changing over from Gas to liquid fuel as the Distilite fuel pump-1 did not start on Auto. |
|  |  | 05.08.09 | 15.04 | 05.08.09 | 15.40 | Exhaust Temperature High |
|  |  | 23.08.09 | 21.15 | 23.08.09 | 23.11 | Gas Restriction |
|  |  | 23.08.09 | 23.11 | 20.09.09 | 00.52 | High vibration at 1800 RPM |
|  |  | 03.10.09 | 06.02 | 03.10.09 | 09.40 | Turbine under speed alarm appeared |
|  |  | 04.10.09 | 01.53 | 04.10.09 | 05.55 | Exhaust Temperature High |
|  |  | 07.10.09 | 20.38 | 08.10.09 | 16.10 | Gas Restriction |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 2 | 30 | 30.10.09 | 15.10 | 30.10.09 | 16.29 | Tripped due to Grid Failure |
|  |  | 04.11.09 | 14.16 | 04.11.09 | 16.25 | Stopped due GAD running high |
|  |  | 04.11.09 | 19.50 | 04.11.09 | 20.35 | Failure of supply to HSD pump |
|  |  | 19.11.09 | 04.32 | 19.11.09 | 15.40 | Gas fuel Pressure low. |
|  |  | 23.11.09 | 00.43 | 23.11.09 | 03.38 | Low lube oil pressure |
|  |  | 30.11.09 | 19.05 | 12.12.09 | 11.35 | Available on liquid fuel |
|  |  | 19.12.09 | 11.05 | 22.12.09 | 19.25 |  |
|  |  | 23.12.09 | 20.45 | 23.12.09 | 22.45 |  |
|  |  | 02.01.10 | 14.07 | 02.01.10 | 14.40 | Exhaust temperature high |
|  |  | 05.01.20 | 17.45 | 05.01.10 | 18.10 | Exhaust temperature high |
|  |  | 05.01.10 | 19.25 | 06.01.10 | 16.01 | To attend IGV & Bleed valve problem |
|  |  | 11.01.10 | 07.28 | 11.01.10 | 07.50 | Exhaust temperature high |
|  |  | 15.01.10 | 14.50 | 16.01.10 | 06.50 | Swapping of gas to PPCL |
|  |  | 16.01.10 | 12.10 | 17.01.10 | 07.05 | Swapping of gas to PPCL |
|  |  | 23.01.10 | 05.58 | 23.01.10 | 15.50 | Stopped due to overloading of 100 MVA transformer-I as the 160 MVA Transformer was under shut down |
|  |  | 23.01.10 | 16.31 | 26.01.10 | 02.40 | Tripped on Exhaust temperature high |
|  |  | 29.01.10 | 14.55 | 29.01.10 | 16.18 | Tripped on lube oil temp.high. |
|  |  | 31.01.10 | 09.05 | 31.01.10 | 19.05 | Available on liquid fuel |
|  |  | 05.02.10 | 15.15 | 05.02.10 | 16.14 | Due to tripping of 100MVA & 160MVA Tx on jerk |
|  |  | 06.02.10 | 11.25 | 06.02.10 | 12.18 | High LTTH |
|  |  | 07.02.10 | 14.05 | 08.02.10 | 00.40 | Available on Open Cycle |
|  |  | 21.02.10 | 07.05 | 21.02.10 | 19.55 | Available on Open Cycle |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 14.46 | Bus Bar differential operation |
|  |  | 08.03.10 | 00.10 | 10.03.10 | 12.10 | Stopped for Excitor Cleaning |
|  |  | 28.03.10 | 03.50 | 28.03.10 | 04.00 | Came on FSNL due to jerk |
|  |  | 29.03.10 | 02.48 | 29.03.10 | 10.25 | Tripped due to tripping of 160 MVA TX. at GT end. |
|  |  | 29.03.10 | 12.50 | 29.03.10 | 14.58 | Tripped on jerk |
| 3 | 30 | 29.04.09 | 00.50 | 29.04.09 | 03.29 | LTTH High |
|  |  | 07.05.09 | 09.02 | 07.05.09 | 22.23 | Swapping of gas to PPCL |
|  |  | 17.05.09 | 12.42 | 17.05.09 | 17.42 | Lube oil temperature high |
|  |  | 19.05.09 | 12.45 | 22.05.09 | 19.40 | Swapping of gas to PPCL |
|  |  | 02.06.09 | 00.25 | 02.06.09 | 19.28 | Swapping of gas to PPCL |
|  |  | 09.06.09 | 23.02 | 10.06.09 | 06.52 | Swapping of gas to PPCL |
|  |  | 12.06.09 | 00.00 | 12.06.09 | 12.13 | Swapping of gas to PPCL |
|  |  | 12.06.09 | 15.15 | 12.06.09 | 20.07 | Due to tripping of 160 MVA Tx at both end |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 14.45 |  |
|  |  | 16.06.09 | 19.10 | 17.06.09 | 09.45 | Swapping of gas to PPCL |
|  |  | 17.06.09 | 19.45 | 18.06.09 | 12.55 | Swapping of gas to PPCL |
|  |  | 21.06.09 | 12.30 | 22.06.09 | 00.28 | Swapping of gas to PPCL |
|  |  | 22.06.09 | 03.00 | 22.06.09 | 09.57 | Swapping of gas to PPCL |
|  |  | 22.06.09 | 22.15 | 23.06.09 | 12.40 | Swapping of gas to PPCL |
|  |  | 29.06.09 | 11.45 | 29.06.09 | 19.27 | To attend leakage in HRSG#3 |
|  |  | 30.06.09 | 01.32 | 30.06.09 | 11.55 | Swapping of gas to PPCL |
|  |  | 30.06.09 | 23.30 | 01.07.09 | 05.58 | Swapping of gas to PPCL |
|  |  | 07.07.09 | 05.42 | 07.07.09 | 13.47 | Malfunctioning of Battery Charger. |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 08.50 | Due to blast in the breaker of 5 MVA |
|  |  | 27.07.09 | 20.50 | 27.07.09 | 23.07 | Tripped on loss of flame. |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 3 | 30 | 15.08.09 | 10.15 | 15.08.09 | 20.55 | Gas Restriction |
|  |  | 21.08.09 | 14.38 | 21.08.09 | 16.58 | Loss of flame |
|  |  | 31.08.09 | 21.50 | 31.08.09 | 23.59 | Tripped without any Audio alarm. |
|  |  | 13.09.09 | 09.50 | 13.09.09 | 10.41 | Tripped due to Grid failure. |
|  |  | 13.09.09 | 11.20 | 13.09.09 | 16.15 | To charge 66 KV Dead Bus |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 12.20 | Tripped due to Grid failure. |
|  |  | 20.09.09 | 09.55 | 21.09.09 | 23.34 | To provide shut down on 160MVA Tx |
|  |  | 13.10.09 | 00.05 | 13.10.09 | 18.40 | Gas restriction |
|  |  | 13.10.09 | 20.05 | 14.10.09 | 20.10 |  |
|  |  | 14.10.09 | 22.05 | 15.10.09 | 18.02 |  |
|  |  | 16.10.09 | 22.03 | 17.10.09 | 18.02 |  |
|  |  | 17.10.09 | 20.08 | 18.10.09 | 18.02 |  |
|  |  | 18.10.09 | 20.05 | 19.10.09 | 18.45 |  |
|  |  | 19.10.09 | 20.05 | 20.10.09 | 18.05 |  |
|  |  | 21.10.09 | 00.01 | 21.10.09 | 18.00 |  |
|  |  | 21.10.09 | 20.05 | 22.10.09 | 17.45 |  |
|  |  | 23.10.09 | 06.10 | 23.10.09 | 11.28 |  |
|  |  | 29.10.09 | 21.02 | 29.10.09 | 23.50 |  |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 15.58 | Tripped due to Grid Failure |
|  |  | 31.10.09 | 07.02 | 31.10.09 | 18.04 | Gas restriction |
|  |  | 01.11.09 | 10.04 | 02.11.09 | 10.15 | Gas restriction |
|  |  | 05.11.09 | 14.05 | 05.11.09 | 14.56 | High LTTH |
|  |  | 05.11.09 | 18.54 | 06.11.09 | 09.40 | Gas restriction |
|  |  | 06.11.09 | 16.35 | 07.11.09 | 12.15 | Gas restriction |
|  |  | 08.11.09 | 00.10 | 08.11.09 | 14.59 | Gas restriction |
|  |  | 13.11.09 | 14.32 | 14.11.09 | 18.40 | Gas restriction |
|  |  | 20.11.09 | 01.46 | 20.11.09 | 18.40 | Gas restriction |
|  |  | 20.11.09 | 11.02 | 24.11.09 | 03.59 | Gas restriction |
|  |  | 05.12.09 | 12.32 | 05.12.09 | 16.51 | To replace Generator absolute filter. |
|  |  | 10.12.09 | 15.47 | 14.12.09 | 07.30 | Available on liquid fire |
|  |  | 14.12.09 | 15.05 | 14.12.09 | 21.20 |  |
|  |  | 15.12.09 | 00.16 | 15.12.09 | 07.45 | Available on liquid fire |
|  |  | 15.12.09 | 15.00 | 16.12.09 | 18.08 |  |
|  |  | 17.12.09 | 00.05 | 21.12.09 | 22.55 |  |
|  |  | 22.12.09 | 19.30 | 02.01.10 | 11.25 |  |
|  |  | 06.01.10 | 12.02 | 06.01.10 | 20.50 | Swapping of gas to PPCL |
|  |  | 07.01.10 | 23.42 | 09.01.10 | 23.15 | Tripped on rotating earth diode fault |
|  |  | 10.01.10 | 19.15 | 11.01.10 | 06.45 | Stopped as generation on liquid fuel is not required |
|  |  | 11.01.10 | 23.10 | 12.01.10 | 07.05 |  |
|  |  | 13.01.10 | 00.05 | 13.01.10 | 07.06 |  |
|  |  | 13.01.10 | 17.01 | 14.01.10 | 09.53 |  |
|  |  | 15.01.10 | 14.52 | 17.01.10 | 19.57 |  |
|  |  | 19.01.10 | 20.29 | 20.01.10 | 06.38 |  |
|  |  | 21.01.10 | 17.45 | 22.01.10 | 06.50 | Swapping of gas to PPCL |
|  |  | 22.01.10 | 16.12 | 23.01.10 | 05.55 | Due to tripping of 160MVA Tx. and after that not taken on load due to overloading of 100 MVA Tx. |
|  |  | 24.01.10 | 14.40 | 24.01.10 | 16.40 | Tripped on LTTH high |
|  |  | 25.01.10 | 19.02 | 26.01.10 | 14.33 | Electrical trouble |
|  |  | 26.01.10 | 14.35 | 27.01.10 | 01.28 | Electrical trouble |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 3 | 30 | 28.01.10 | 06.10 | 28.01.10 | 06.45 | Tripped on high TAD |
|  |  | 05.02.10 | 07.46 | 05.02.10 | 15.52 | Tripped on loss of Excitation field |
|  |  | 05.02.10 | 15.55 | 05.02.10 | 16.12 | Due to heavy jerk in the system 100 MVA and 160 MVA Transformer tripped resulting in failure of auxiliary supply and machine tripped. |
|  |  | 08.02.10 | 19.52 | 08.02.10 | 20.52 | Tripped on high TAD |
|  |  | 17.02.10 | 23.02 | 18.02.10 | 18.05 | Available on Liquid Fuel |
|  |  | 20.02.10 | 17.02 | 22.02.10 | 19.05 | Available on Liquid Fuel |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 16.07 | tripped on over speed |
|  |  | 26.03.10 | 10.10 | 26.03.10 | 14.30 | Battery under voltage alarm |
|  |  | 29.03.10 | 02.48 | 29.03.10 | 05.40 | Tripped due to tripping of 160 MVA TX. at GT end. |
|  |  | 29.03.10 | 10.25 | 29.03.10 | 16.40 | Stopped to clean PHE. |
|  |  | 29.03.10 | 16.48 | 29.03.10 | 19.45 | Loss of flame. |
|  |  | 10.04.09 | 11.32 | 10.04.09 | 15.20 | Gas Restriction |
|  |  | 08.05.09 | 09.10 | 09.05.09 | 01.20 | Swapping of gas to PPCL |
|  |  | 10.05.09 | 17.24 | 10.05.09 | 20.25 | High exhaust temperature |
|  |  | 13.05.09 | 22.10 | 13.05.09 | 23.59 | Swapping of gas to PPCL |
|  |  | 24.05.09 | 11.05 | 25.05.09 | 21.20 | Gas Restriction |
|  |  | 31.05.09 | 08.35 | 31.05.09 | 08.42 | To close 66 KV Bus Coupler. |
|  |  | 13.06.09 | 06.10 | 13.06.09 | 18.20 | Swapping of gas to PPCL |
|  |  | 14.06.09 | 15.04 | 16.06.09 | 02.38 | Swapping of gas to PPCL |
| 4 | 30 | 26.06.09 | 01.100 | 26.06.09 | 13.27 | Swapping of gas to PPCL |
|  |  | 04.07.09 | 16.25 | 05.07.09 | 20.02 | Swapping of gas to PPCL |
|  |  | 05.07.09 | 20.28 | 07.07.09 | 19.50 | Lube oil pressure low |
|  |  | 13.07.09 | 16.03 | 28.07.09 | 15.28 | High exhaust temperature |
|  |  | 11.08.09 | 13.55 | 11.08.09 | 18.50 | Electrical trouble |
|  |  | 21.08.09 | 16.39 | 21.08.09 | 18.37 | Electrical trouble |
|  |  | 21.08.09 | 18.40 | 21.08.09 | 22.15 | Electrical trouble |
|  |  | 10.09.09 | 16.25 | 10.09.09 | 18.57 | Came on FSNL & reverse power operated on protection panel. |
|  |  | 13.09.09 | 09.50 | 13.09.09 | 14.10 | Came on FSNL due to Grid failure |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 12.25 | Tripped due to Grid failure |
|  |  | 20.09.09 | 01.15 | 21.09.09 | 22.50 | Swapping of gas to PPCL. |
|  |  | 24.09.09 | 13.58 | 24.09.09 | 16.15 | To check load hunting |
|  |  | 27.09.09 | 20.10 | 29.09.09 | 11.07 | Swapping of gas to PPCL. |
|  |  | 29.09.09 | 11.41 | 29.09.09 | 12.40 | Gas fuel hydraulic trip pressure low |
|  |  | 29.09.09 | 13.33 | 29.09.09 | 16.10 | Gas fuel hydraulic trip pressure low |
|  |  | 04.10.09 | 13.40 | 07.10.09 | 19.20 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 09.10.09 | 14.26 | 09.10.09 | 19.02 |  |
|  |  | 10.10.09 | 11.05 | 10.10.09 | 19.12 |  |
|  |  | 11.10.09 | 03.50 | 11.10.09 | 18.25 |  |
|  |  | 15.10.09 | 20.40 | 16.10.09 | 18.50 |  |
|  |  | 22.10.09 | 07.05 | 22.10.09 | 17.55 |  |
|  |  | 23.10.09 | 06.15 | 23.10.09 | 09.50 |  |
|  |  | 24.10.09 | 08.09 | 24.10.09 | 10.55 |  |
|  |  | 25.10.09 | 07.20 | 25.10.09 | 18.02 |  |
|  |  | 25.10.09 | 21.47 | 26.10.09 | 09.45 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 25.10.09 | 21.47 | 26.10.09 | 09.45 |  |
|  |  | 27.10.09 | 08.02 | 27.10.09 | 21.08 |  |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 16.27 |  |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 4 | 30 | 02.11.09 | 18.00 | 03.11.09 | 11.30 |  |
|  |  | 03.11.09 | 11.30 | 05.11.09 | 18.45 |  |
|  |  | 09.11.09 | 00.35 | 10.11.09 | 18.18 |  |
|  |  | 10.11.09 | 20.15 | 11.11.09 | 18.58 |  |
|  |  | 12.11.09 | 00.40 | 13.11.09 | 07.25 |  |
|  |  | 15.11.09 | 01.05 | 18.11.09 | 14.05 |  |
|  |  | 03.12.09 | 13.00 | 03.12.09 | 15.35 | Stopped to replace Generator absolute filter. |
|  |  | 12.12.09 | 11.50 | 14.12.09 | 07.37 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 14.12.09 | 15.05 | 14.12.09 | 21.10 |  |
|  |  | 15.12.09 | 00.20 | 15.12.09 | 07.20 |  |
|  |  | 15.12.09 | 15.00 | 16.12.09 | 17.42 |  |
|  |  | 17.12.09 | 00.07 | 19.12.09 | 07.40 |  |
|  |  | 23.12.09 | 22.50 | 24.12.09 | 18.45 |  |
|  |  | 25.12.09 | 01.25 | 25.12.09 | 07.05 |  |
|  |  | 02.01.10 | 19.05 | 04.01.10 | 00.45 |  |
|  |  | 04.01.10 | 06.30 | 04.01.10 | 10.55 | Due to swapping of gas to PPCL |
|  |  | 04.01.10 | 15.15 | 05.01.10 | 09.00 |  |
|  |  | 05.01.10 | 13.10 | 05.01.10 | 20.00 |  |
|  |  | 06.01.10 | 23.10 | 07.01.10 | 06.59 |  |
|  |  | 07.01.10 | 23.05 | 07.01.10 | 23.58 |  |
|  |  | 14.01.10 | 08.41 | 14.01.10 | 21.00 | Tripped on Generator under voltage alarm |
|  |  | 22.01.10 | 16.12 | 22.01.10 | 17.21 | Due to tripping of 160 MVA Tx |
|  |  | 27.01.10 | 16.31 | 28.01.10 | 21.10 | Tripped on loss of flame |
|  |  | 04.02.10 | 00.05 | 05.02.10 | 14.10 | Swapping of gas to PPCL |
|  |  | 05.02.10 | 15.55 | 05.02.10 | 16.40 | Due to heavy jerk in the system 100 MVA and 160 MVA Transformer tripped resulting in failure of auxiliary supply and machine tripped. |
|  |  | 06.02.10 | 01.14 | 06.02.10 | 03.28 | Gas fuel hydraulic trip pressure low |
|  |  | 06.02.10 | 11.25 | 06.02.10 | 14.40 | Failure of Auxiliary supply. |
|  |  | 18.02.10 | 06.15 | 18.02.10 | 07.54 | Available on Open Cycle |
|  |  | 24.02.10 | 14.43 | 31.03.10 | 23.59 | Electrical trouble normal shut down. |
| 5 | 30 | 18.04.09 | 06.02 | 18.04.09 | 11.45 | HRSG Leakage |
|  |  | 24.04.09 | 08.02 | 24.04.09 | 19.30 | Due to planned shut-down of 220/66kV 160MVA Pr. Tr. |
|  |  | 26.04.09 | 09.35 | 26.04.09 | 21.18 |  |
|  |  | 09.05.09 | 00.56 | 09.05.09 | 17.25 | C&I Problem |
|  |  | 10.05.09 | 14.52 | 10.05.09 | 17.15 | High exhaust temp. |
|  |  | 31.05.09 | 08.32 | 31.05.09 | 12.38 | To close 66 KV Bus Coupler |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 15.10 | Due to tripping of 100 MVA Tx. |
|  |  | 16.07.09 | 11.45 | 16.07.09 | 23.05 | C&I problem |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 06.45 | Due to blast in the breaker of 5 MVA in switch gear room.. |
|  |  | 10.09.09 | 20.05 | 10.09.09 | 21.07 | Swapping of gas to PPCL. |
|  |  | 12.09.09 | 13.17 | 13.09.09 | 11.53 | Swapping of gas to PPCL. |
|  |  | 15.09.09 | 10.32 | 16.09.09 | 10.52 | Swapping of gas to PPCL. |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 12.00 | Swapping of gas to PPCL. |
|  |  | 09.10.09 | 11.10 | 09.10.09 | 18.25 | Hydraulic Protection Trouble and Lube oil header temperature low |
|  |  | 28.10.09 | 01.05 | 28.10.09 | 17.35 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 16.04 |  |
|  |  | 04.11.09 | 20.36 | 06.11.09 | 09.52 |  |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 5 | 30 | 06.11.09 | 12.45 | 09.11.09 | 19.10 |  |
|  |  | 10.11.09 | 20.45 | 11.11.09 | 00.50 |  |
|  |  | 12.11.09 | 05.56 | 12.11.09 | 19.15 |  |
|  |  | 24.11.09 | 13.02 | 25.11.09 | 23.12 |  |
|  |  | 26.11.09 | 10.46 | 01.12.09 | 14.35 |  |
|  |  | 06.12.09 | 14.40 | 06.12.09 | 16.04 | Stopped to attend Mark-IV system |
|  |  | 21.12.09 | 12.45 | 23.12.09 | 23.40 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 25.12.09 | 09.05 | 01.01.10 | 10.55 |  |
|  |  | 04.01.10 | 00.10 | 05.01.10 | 09.01 | SF-6 pressure low alarm. |
|  |  | 09.01.10 | 18.50 | 10.01.10 | 07.00 | Stopped as generation on liquid fuel is not required |
|  |  | 10.01.10 | 19.02 | 11.01.10 | 07.05 |  |
|  |  | 13.01.10 | 00.07 | 13.01.10 | 07.05 | Swapping of gas to PPCL |
|  |  | 13.01.10 | 16.46 | 13.01.10 | 18.20 | Loss of flame |
|  |  | 13.01.10 | 18.20 | 14.01.10 | 06.54 | Not taken on load due to as the generation on liquid fuel is not required by SLDC |
|  |  | 16.01.10 | 11.35 | 16.01.10 | 15.45 | Electrical trouble |
|  |  | 17.01.10 | 02.38 | 17.01.10 | 03.25 | Tripped at high TAD |
|  |  | 18.01.10 | 05.01 | 02.03.10 | 19.05 | Loss of flame and high vibration |
|  |  | 04.03.10 | 01.53 | 04.03.10 | 17.35 | High exhaust temperature |
|  |  | 29.3.10 | 02.48 | 29.03.10 | 13.55 | Tripped due to tripping of 160 MVA TX. at GT end. |
|  |  | 31.03.10 | 22.10 | 31.03.10 | 23.59 | Hydraulic pressure low |
| 6 | 30 | 29.04.09 | 17.26 | 29.04.09 | 22.55 | Electrical Fault |
|  |  | 09.05.09 | 14.32 | 09.05.09 | 23.59 | To install ABT -complaint meters. |
|  |  | 10.05.09 | 15.35 | 10.05.09 | 16.43 | Tripped without out any alarm |
|  |  | 11.05.09 | 22.02 | 12.05.09 | 17.44 | Swapping of gas to PPCL |
|  |  | 16.05.09 | 00.32 | 16.05.09 | 13.46 | Swapping of gas to PPCL |
|  |  | 26.05.09 | 14.31 | 26.05.09 | 17.50 | To replace Gen. differential relay. |
|  |  | 31.05.09 | 08.35 | 31.05.09 | 08.42 | To close 66 KV Bus Coupler. |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 14.10 | Tripping of 100MVA Tx at both end. |
|  |  | 30.06.09 | 2330 | 01.07.09 | 06.42 | Swapping of gas to PPCL |
|  |  | 12.07.09 | 02.40 | 12.07.09 | 14.25 | Loss of Excitation |
|  |  | 19.07.09 | 13.28 | 19.07.09 | 13.50 | FSNL due to Gen. Over heating alarm appearing on protection panel |
|  |  | 19.07.09 | 17.50 | 19.07.09 | 18.35 |  |
|  |  | 29.07.09 | 15.40 | 29.07.09 | 20.25 | Electrical Problem |
|  |  | 21.08.09 | 16.37 | 22.08.09 | 19.40 | Tripped on preignition pressure p-2 high and Battery ground alarm |
|  |  | 04.09.09 | 18.15 | 06.09.09 | 15.55 | Gas Restriction |
|  |  | 10.09.09 | 20.15 | 11.09.09 | 19.20 | Lss of excitation. |
|  |  | 13.09.09 | 09.50 | 13.09.09 | 10.43 | Came on FSNl due to Grid failure |
|  |  | 16.09.09 | 06.04 | 16.09.09 | 15.20 | Gas Restriction |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 12.32 | Tripped due to failure of Grid |
|  |  | 17.09.09 | 22.20 | 17.09.09 | 23.40 | Loss of Excitation |
|  |  | 26.09.09 | 08.05 | 26.09.09 | 08.21 | Came on FSNL due to jerk |
|  |  | 28.09.09 | 18.55 | 29.09.09 | 12.05 | Gas Restriction |
|  |  | 13.10.09 | 00.06 | 13.10.09 | 15.15 | Gas Restriction |
|  |  | 14.10.09 | 23.46 | 15.10.09 | 06.10 | Gas Restriction |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 15.37 | Tripped due to Grid Failure |
|  |  | 03.11.09 | 16.13 | 04.11.09 | 15.18 | Stopped as liquid fuel generation not required by SLDC |
|  |  | 12.11.09 | 06.32 | 14.11.09 | 00.02 |  |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 6 | 30 | 14.11.09 | 05.58 | 15.11.09 | 22.05 |  |
|  |  | 16.11.09 | 12.05 | 23.11.09 | 00.05 |  |
|  |  | 23.11.09 | 14.35 | 30.11.09 | 11.50 |  |
|  |  | 24.12.09 | 00.40 | 24.12.09 | 16.05 | Swapping of gas to PPCL |
|  |  | 02.01.10 | 19.05 | 03.01.10 | 18.55 | Stopped due to swapping of gas to PPCL |
|  |  | 05.01.10 | 13.05 | 06.01.10 | 06.42 |  |
|  |  | 06.01.10 | 19.05 | 07.01.10 | 06.57 |  |
|  |  | 07.01.10 | 23.05 | 08.01.10 | 07.00 |  |
|  |  | 08.01.10 | 07.00 | 08.01.10 | 13.10 | Problem in Diesel Engine |
|  |  | 09.01.10 | 00.02 | 09.01.10 | 06.59 | Stopped due to swapping of gas to PPCL |
|  |  | 14.01.10 | 15.16 | 15.01.10 | 17.30 |  |
|  |  | 15.01.10 | 17.45 | 16.01.10 | 06.57 |  |
|  |  | 16.01.10 | 16.37 | 17.01.10 | 07.15 |  |
|  |  | 17.01.10 | 14.02 | 18.01.10 | 13.50 |  |
|  |  | 19.01.10 | 13.30 | 19.01.10 | 18.58 |  |
|  |  | 22.01.10 | 17.05 | 22.01.10 | 18.05 |  |
|  |  | 27.01.10 | 01.35 | 27.01.10 | 06.45 | Available on open cycle. |
|  |  | 05.02.10 | 15.15 | 05.02.10 | 16.51 | Due to heavy jerk, 100 MVA and 160 MVA Transformer tripped |
|  |  | 09.02.10 | 11.55 | 10.02.10 | 01.48 | Available of Open Cycle |
|  |  | 24.02.10 | 00.00 | 24.02.10 | 17.6 | Tripped on bus bar differential relay operated. |
|  |  | 03.03.10 | 22.05 | 04.03.10 | 03.10 | Stopped for exciter cleaning |
|  |  | 04.03.10 | 22.32 | 06.03.10 | 23.59 | Stopped for exciter cleaning |
|  |  | 26.03.10 | 00.02 | 26.03.10 | 05.34 | Stopped for PHE Cleaning |
|  |  | 29.03.10 | 03.16 | 29.03.10 | 13.40 | Tripped due to LTTH high. |
| STG1 | 34 | 06.04.09 | 10.30 | 08.04.09 | 12.00 | BTL |
|  |  | 21.04.09 | 00.05 | 22.04.09 | 21.10 | Maintenance work |
|  |  | 28.04.09 | 08.33 | 29.04.09 | 16.20 | HRSG Leakage |
|  |  | 30.04.09 | 11.58 | 30.04.09 | 12.28 | AVR System Problem |
|  |  | 01.05.09 | 16.58 | 01.05.09 | 20.33 | Tripped due to CEP 1-A tripped. |
|  |  | 03.05.09 | 23.10 | 04.05.09 | 04.40 | Tripped due to disappearance of drum parameters |
|  |  | 05.05.09 | 08.01 | 06.05.09 | 01.05 | Stopped due to stopping of GT-1 since only HRSG-I in service. |
|  |  | 13.05.09 | 11.20 | 13.05.09 | 14.27 | Tripped while change over Auxiliary supply from 7.5 MVA to 20 MVA. |
|  |  | 13.05.09 | 18.06 | 13.05.09 | 19.40 | Tripped on false alarm of HRSG# I |
|  |  | 22.05.09 | 19.42 | 22.05.09 | 22.05 | Malfunctioning of parameters |
|  |  | 31.05.09 | 08.35 | 31.05.09 | 21.28 | Failure of 800 KVA transformer. |
|  |  | 02.06.09 | 18.13 | 02.06.09 | 19.20 | Due to tripping of BFP-1A & HRSG# 1 & 2. |
|  |  | 06.06.09 | 22.02 | 07.06.09 | 23.40 | Stopped to attend various leakages. |
|  |  | 12.06.09 | 15.15 | 12.06.09 | 16.53 | Due to tripping of 160 MVA Tx at both end |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 14.42 | Due to tripping of 100 MVA Tx. |
|  |  | 20.06.09 | 06.02 | 20.06.09 | 23.48 | Stopped to attend various leakages. |
|  |  | 26.06.09 | 04.05 | 26.06.09 | 04.25 | Tripped on low hot well level |
|  |  | 30.06.09 | 13.00 | 30.06.09 | 20.05 | To attend leakage at PRDS station |
|  |  | 09.07.09 | 04.45 | 09.07.09 | 08.20 | Due to malfunctioning of parameters |
|  |  | 14.07.09 | 00.05 | 17.07.09 | 17.25 | Toto attend tube leakage in HRSG#2 |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 07.58 | Due to blast in the breaker of 5 MVA in switch gear room.. |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| STG1 | 34 | 21.07.09 | 08.38 | 21.07.09 | 09.28 | Tripped due to tripping of 800 KVA transformer on instantaneous O/C |
|  |  | 28.07.09 | 18.05 | 28.07.09 | 18.26 | Due to tripping of 7.5 MVA Tx |
|  |  | 09.08.09 | 17.55 | 09.08.09 | 19.47 | Tripped due to alarm of GT-1 Tripped appeared on STG# I BCD which led to tripping of HRSG-I & subsequently STG# I. |
|  |  | 23.08.09 | 00.05 | 24.08.09 | 19.10 | To attend PRDS leakage. |
|  |  | 26.08.09 | 02.15 | 26.08.09 | 05.05 | Tripped due to Closing of MS-1 Valve |
|  |  | 26.08.09 | 18.05 | 26.08.09 | 19.52 | Channel-I & II operated. |
|  |  | 27.08.09 | 08.15 | 27.08.09 | 12.55 | Tripped though all the parameters were normal at BCD. |
|  |  | 27.08.09 | 15.05 | 27.08.09 | 20.50 | Control Oil pressure very low |
|  |  | 28.08.09 | 04.32 | 28.08.09 | 06.35 | Tripped due to tripping of GT# 1. |
|  |  | 01.09.09 | 22.35 | 02.09.09 | 04.55 | Tripped due to tripping of GT# 1 |
|  |  | 02.09.09 | 07.31 | 02.09.09 | 22.55 | C&I Problem |
|  |  | 07.09.09 | 02.20 | 07.09.09 | 20.04 | Tripped due to GT# 1came on FSNL |
|  |  | 13.09.09 | 09.50 | 14.09.09 | 06.40 | Tripped due to Grid failure. |
|  |  | 14.09.09 | 13.52 | 14.09.09 | 19.05 | Exhaust Steam Pressure High. |
|  |  | 17.09.09 | 10.54 | 18.09.09 | 00.20 | Tripped during Grid failure |
|  |  | 28.09.09 | 10.05 | 28.09.09 | 11.52 | Turbine shaft vibration very high. |
|  |  | 30.10.09 | 02.40 | 30.10.09 | 04.33 | Tripped due to failure of BK Card |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 16.25 | Tripped due to Grid Failure |
|  |  | 04.11.09 | 19.50 | 04.11.09 | 21.20 | Due to tripping of GT-I & II |
|  |  | 09.11.09 | 22.25 | 10.11.09 | 02.46 | Due to choke of suction strainer of both BFPs. |
|  |  | 10.11.09 | 09.11 | 10.11.09 | 11.50 | Low Vacuum |
|  |  | 01.12.09 | 18.15 | 11.12.09 | 20.45 | Stopped for condenser cleaning |
|  |  | 14.12.09 | 00.15 | 14.12.09 | 03.35 | Channel-I& II operated |
|  |  | 19.12.09 | 05.06 | 19.12.09 | 05.58 |  |
|  |  | 19.12.09 | 08.05 | 19.12.09 | 08.55 |  |
|  |  | 24.12.09 | 17.08 | 24.12.09 | 18.32 |  |
|  |  | 26.12.09 | 14.05 | 26.12.09 | 16.10 | Stopped to attend hot spot |
|  |  | 21.01.10 | 09.35 | 21.01.10 | 10.50 | tripped on Ch-I and II |
|  |  | 31.01.10 | 09.05 | 02.02.10 | 03.35 | Stopped to attend leakages in CPH |
|  |  | 05.02.10 | 15.55 | 05.02.10 | 16.58 | Due to heavy jerk in the system 100 MVA and 160 MVA Transformer tripped resulting in failure of auxiliary supply and machine tripped. |
|  |  | 06.02.10 | 11.25 | 06.02.10 | 13.15 | Failure of Auxiliary supply. |
|  |  | 06.02.10 | 19.40 | 06.02.10 | 20.20 | Failure of Auxiliary supply. |
|  |  | 15.02.10 | 17.26 | 15.02.10 | 18.10 | Tripped due to tripping of VB-II radial feeder relay 51& 64 operated. |
|  |  | 20.02.10 | 01.15 | 20.02.10 | 04.35 | Tripped as AOP-I tripped due to jerk in the control Room as VB-I tripped. |
|  |  | 20.02.10 | 16.43 | 20.02.10 | 17.15 | Control oil header pressure low. |
|  |  | 20.02.10 | 17.55 | 20.02.10 | 22.15 | Control oil header pressure low. |
|  |  | 21.02.10 | 06.40 | 21.02.10 | 20.05 | Stopped to install flow meter to measure DM Water and to arrend other leakages. |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 16.55 | Bus bar differential relay operated. |
|  |  | 25.02.10 | 13.15 | 25.02.10 | 14.20 | Tripped in the jerk due snapping of conductor of VB-II |
|  |  | 25.02.10 | 15.05 | 25.02.10 | 20.20 | C&I department |
|  |  | 26.03.10 | 18.45 | 26.03.10 | 19.15 | Tripped due to tripping of AC-AOP-IB |
|  |  | 29.03.10 | 02.48 | 29.03.10 | 17.28 | Tripped due to tripping of 160 MVA TX. at GT end. |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| STG2 | 34 | 07.04.09 | 00.05 | 08.04.09 | 22.02 | To attend leakage |
|  |  | 10.04.09 | 02.02 | 10.04.09 | 02.40 | Class A relay group-2 operated |
|  |  | 30.04.09 | 11.58 | 30.04.09 | 12.28 | Class 'B' trip relay operated& 40G |
|  |  | 06.05.09 | 09.05 | 06.05.09 | 21.06 | To install ABT -complaint meters. |
|  |  | 13.05.09 | 11.20 | 13.05.09 | 11.40 | Tripped while change over of Auxiliary supply from 7.5 MVA to 20 MVA. |
|  |  | 29.05.09 | 19.24 | 29.05.09 | 20.20 | Tripped due to following relay i) Generator class-A group-II 86GA-2. |
|  |  | 29.05.09 | 20.31 | 29.05.09 | 21.55 |  |
|  |  | 31.05.09 | 07.37 | 31.05.09 | 09.55 | Due to tripping of 100 MVA Tx-II. |
|  |  | 02.06.09 | 17.09 | 02.06.09 | 19.05 | Due to tripping of HRSG# 4. |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 17.05 | Due to tripping of 100 MVA Tx. |
|  |  | 07.07.09 | 05.44 | 07.07.09 | 15.28 | Tripped due to tripping of GT# 3 |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 12.08 | Due to blast in the breaker of 5 MVA in switch gear room. |
|  |  | 21.07.09 | 08.38 | 21.07.09 | 09.18 | Tripped due to tripping of 800 KVA transformer on instantaneous O/C |
|  |  | 23.07.09 | 12.27 | 23.07.09 | 13.13 | Tripped without any abnormality of system. |
|  |  | 27.07.09 | 20.50 | 28.07.09 | 00.28 | Tripped due to tripping of GT# 3 which is tripped on loss of flame. |
|  |  | 28.07.09 | 18.05 | 28.07.09 | 18.20 | Due to tripping of 7.5 MVA Tx. |
|  |  | 31.07.09 | 13.32 | 31.07.09 | 19.15 | To attend the condensate water transfer problem from hot well to dearater. |
|  |  | 15.08.09 | 21.25 | 15.08.09 | 22.28 | Drum level very high. |
|  |  | 16.08.09 | 13.32 | 16.08.09 | 14.15 | Due to tripping of BFP-2B. |
|  |  | 21.08.09 | 16.39 | 21.08.09 | 17.52 | Due to tripping of GT#4. |
|  |  | 26.08.09 | 14.10 | 27.08.09 | 23.59 | Shortage of DM water |
|  |  | 13.09.09 | 09.50 | 13.09.08 | 17.55 | Tripped due to Grid failure. |
|  |  | 17.09.09 | 10.54 | 17.09.09 | 13.50 | Tripped due to Grid failure. |
|  |  | 20.09.09 | 09.55 | 22.09.09 | 11.05 | Swapping of gas to PPCL. |
|  |  | 21.10.09 | 10.02 | 23.10.09 | 14.29 | Parameter of HRSG-4 disappeared while resetting these, Boiler-4 tripped consequently STG tripped |
|  |  | 30.10.09 | 15.10 | 30.10.09 | 21.25 | Tripped due to Grid Failure |
|  |  | 05.11.09 | 14.05 | 05.11.09 | 15.32 | Tripped due to tripping of GT# 3 |
|  |  | 05.11.09 | 17.31 | 05.11.09 | 19.55 | Stopped to attend leakages |
|  |  | 06.11.09 | 17.02 | 06.11.09 | 18.50 | To clean suction strainer of CEP |
|  |  | 07.11.09 | 17.01 | 07.11.09 | 20.10 | Stopped to attend leakages |
|  |  | 14.11.09 | 00.57 | 14.11.09 | 07.40 | Heavy leakage from flange of SRV |
|  |  | 21.11.09 | 05.17 | 21.11.09 | 21.45 | Due to failure of fuse of Power Distribution Module |
|  |  | 12.12.09 | 11.50 | 23.12.09 | 03.00 | Stopped for condenser cleaning |
|  |  | 23.12.09 | 02.02 | 23.12.09 | 18.30 | Exhaust steam pressure high. |
|  |  | 23.12.09 | 18.40 | 24.12.09 | 23.55 | Due to problem in governing system |
|  |  | 25.12.09 | 00.50 | 25.12.09 | 08.55 | Machine tripped due to load not increased |
|  |  | 04.01.10 | 06.45 | 04.01.10 | 07.58 | tripped due to field failure relay |
|  |  | 05.01.10 | 16.30 | 05.01.10 | 23.26 | tripped on Ch-I and II |
|  |  | 05.01.10 | 23.58 | 06.01.10 | 10.50 | Manually tripped as there was hunting in the load |
|  |  | 06.01.10 | 12.03 | 06.01.10 | 12.38 | tripped on Ch-I and II |
|  |  | 06.01.10 | 14.16 | 06.01.10 | 15.59 | Axial shift very high |
|  |  | 06.01.10 | 17.02 | 06.01.10 | 18.45 | Low vacuum |
|  |  | 07.01.10 | 23.42 | 08.01.10 | 00.28 | Tripped due to tripping of GT-3 |
|  |  | 10.01.10 | 11.44 | 10.01.10 | 12.18 | due to tripping of HRSG-4 and there rafter CEP-2A without any alarm |
|  |  | 11.01.10 | 15.45 | 11.01.10 | 18.25 | Stopped due to choking of CEPs. |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| STG2 | 34 | 14.01.10 | 08.41 | 14.01.10 | 11.52 | Tripped due to tripping of GT-4 |
|  |  | 22.01.10 | 16.12 | 22.01.10 | 18.31 | Due to tripping of 160 MVA Tx |
|  |  | 28.01.10 | 06.10 | 28.01.10 | 07.33 | High TAD |
|  |  | 31.01.10 | 15.48 | 31.01.10 | 16.55 | Low vacuum |
|  |  | 05.02.10 | 07.46 | 05.02.10 | 18.50 | Tripped due to tripping of GT#3 |
|  |  | 05.02.10 | 19.54 | 05.02.10 | 23.12 | Tripped on Ch-I and II. |
|  |  | 06.02.10 | 11.25 | 06.02.10 | 14.30 | Failure of Auxiliary supply. |
|  |  | 06.02.10 | 19.40 | 06.02.10 | 20.15 | Failure of Auxiliary supply. |
|  |  | 18.02.10 | 06.15 | 18.02.10 | 19.55 | Stopped to attend various leakages |
|  |  | 22.02.10 | 11.18 | 22.02.10 | 12.05 | Tripped on Ch-I and II. |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 17.35 | Bus bar differential relay operated. |
|  |  | 03.06.10 | 12.02 | 03.06.10 | 12.45 | Lube oil header pressure very low. |
|  |  | 13.03.10 | 11.32 | 13.03.10 | 16.37 | Stopped to attend leakages |
|  |  | 24.03.10 | 09.25 | 24.03.10 | 18.55 | Stopped to attend SRV of HRSG#4 |
|  |  | 25.03.10 | 15.50 | 25.03.10 | 16.55 | Trip Oil pressure very low. |
|  |  | 26.03.10 | 10.10 | 26.03.10 | 16.20 | Tripped due to tripping of GT-3 |
|  |  | 29.03.10 | 02.48 | 30.03.10 | 00.35 | Tripped due to tripping of 160 MVA TX. at GT end. |
| STG3 | 34 | 05.05.09 | 16.15 | 05.05.09 | 16.50 | To install ABT -complaint meters. |
|  |  | 09.05.09 | 09.02 | 09.05.09 | 21.25 | To attend leakages |
|  |  | 10.05.09 | 15.35 | 10.05.09 | 19.15 | Due to tripping of GT No. 6. |
|  |  | 11.05.09 | 17.42 | 11.05.09 | 18.35 | Tripped due to disappearance of hot well level parameters. |
|  |  | 13.05.09 | 11.20 | 13.05.09 | 12.40 | Tripped while change over of Auxiliary supply from 7.5 MVA to 20 MVA. |
|  |  | 31.05.09 | 08.35 | 31.05.09 | 10.29 | Due to failure of 800 KVA Tx |
|  |  | 12.06.09 | 15.15 | 12.06.09 | 18.20 | Tripped due to 160 MVA Tx at both end |
|  |  | 15.06.09 | 13.30 | 15.06.09 | 16.12 | Due to tripping of 100 MVA Tx. |
|  |  | 19.07.09 | 05.29 | 19.07.09 | 08.28 | Due to blast in the breaker of 5 MVA in switch gear room.. |
|  |  | 21.07.09 | 08.38 | 21.07.09 | 09.35 | Tripped due to tripping of 800 KVA transformer on instantaneous O/C |
|  |  | 23.07.09 | 14.02 | 23.07.09 | 21.50 | Generator class -A relay operated. |
|  |  | 28.07.09 | 18.05 | 28.07.09 | 18.35 | Due to tripping of 7.5 MVA Tx. |
|  |  | 28.08.09 | 03.10 | 11.09.09 | 02.02 | Axial Shift Problem |
|  |  | 12.09.09 | 06.16 | 19.09.09 | 14.13 | Channel-I & II operated |
|  |  | 25.10.09 | 13.05 | 26.10.09 | 13.25 | Control oil header pressure low |
|  |  | 25.10.09 | 23.31 | 26.10.09 | 15.10 | Low vacuum |
|  |  | 27.10.09 | 17.37 | 27.10.09 | 18.40 | Low vacuum |
|  |  | 30.10.09 | 15.10 | 31.10.09 | 14.40 | Tripped due to Grid Failure |
|  |  | 02.11.09 | 11.57 | 03.11.09 | 00.10 | To attend leakages and Condenser back washing |
|  |  | 10.11.09 | 23.28 | 11.11.09 | 00.20 | Low Vacuum |
|  |  | 11.11.09 | 17.01 | 11.11.09 | 23.40 | To attend leakages |
|  |  | 12.11.09 | 00.45 | 12.11.09 | 23.50 | Exhaust Temperature High |
|  |  | 24.11.09 | 12.55 | 01.12.09 | 04.05 | Stopped for Condenser cleaning |
|  |  | 31.12.09 | 03.15 | 31.12.09 | 09.25 | Axial shift very high |
|  |  | 01.01.10 | 06.02 | 01.01.10 | 06.53 | Tripped on sudden throw off load and Class-A relay operated |
|  |  | 07.01.10 | 06.00 | 07.01.10 | 22.46 | Stopped to attend leakages |
|  |  | 17.01.10 | 02.38 | 17.01.10 | 04.05 | Tripped due to tripping of GT-5 |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| STG3 | 34 | 18.01.10 | 05.01 | 18.01.10 | 17.20 | Tripped due to tripping of GT-5 |
|  |  | 19.1.10 | 13.28 | 19.01.10 | 21.32 | Stopped as GT-6 stopped by SLDC |
|  |  | 22.01.10 | 16.12 | 22.01.10 | 20.20 | Due to tripping of 160 MVA Tx |
|  |  | 26.01.10 | 17.20 | 28.01.10 | 00.11 | Tripped on Generator Stator E/F |
|  |  | 03.02.10 | 19.10 | 03.02.10 | 21.42 | Manually tripped as BFP-3A was tripping frequently. |
|  |  | 05.02.10 | 15.55 | 05.02.10 | 18.12 | Due to heavy jerk in the system 100 MVA and 160 MVA Transformer tripped resulting in failure of auxiliary supply and machine tripped. |
|  |  | 06.02.10 | 11.25 | 06.02.10 | 19.15 | Failure of Auxiliary supply. |
|  |  | 09.02.10 | 11.50 | 10.02.10 | 07.05 | Mechanical problem |
|  |  | 24.02.10 | 14.43 | 24.02.10 | 19.05 | Bus bar differential relay operated. |
|  |  | 26.02.10 | 13.10 | 26.02.10 | 15.10 | Tripped due to Stand by Transformer earth fault relay. |
|  |  | 04.03.10 | 01.53 | 04.03.10 | 04.58 | Tripped due to tripping of GT-5 |
|  |  | 12.03.10 | 18.02 | 12.03.10 | 20.55 | Tripped on low vacuum |
|  |  | 29.03.10 | 02.48 | 29.03.10 | 15.50 | Tripped due to tripping of 160 MVA TX. at GT end. |

(D)   PRAGATI STATION

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
| 1 | 104 | Date | Time | Date | Time |  |
|  |  | 18.04.09 | 15.42 | 18.04.09 | 16.26 | Tripped due to jerk |
|  |  | 27.04.09 | 10.48 | 28.04.09 | 13.25 | Hydraulic Pressure Low |
|  |  | 19.05.09 | 20.55 | 19.05.09 | 22.17 | Tripped due to tripping of associated transmission lines |
|  |  | 25.05.09 | 21.29 | 25.05.09 | 22.56 | Tripped due to tripping of associated transmission lines |
|  |  | 05.06.09 | 02.48 | 05.06.09 | 10.07 |  |
|  |  | 03.07.09 | 07.28 | 03.07.09 | 12.27 |  |
|  |  | 04.07.09 | 11.42 | 04.07.09 | 12.01 |  |
|  |  | 06.07.09 | 14.10 | 06.07.09 | 14.28 |  |
|  |  | 14.07.09 | 09.42 | 14.07.09 | 10.18 |  |
|  |  | 05.08.09 | 16.15 | 05.08.09 | 17.37 |  |
|  |  | 10.08.09 | 19.09 | 10.08.09 | 19.25 |  |
|  |  | 12.08.09 | 15.15 | 12.08.09 | 16.31 |  |
|  |  | 20.08.09 | 21.16 | 22.08.09 | 11.02 | Internal Fault |
|  |  | 22.08.09 | 18.17 | 22.08.09 | 20.10 | Internal Fault |
|  |  | 27.08.09 | 18.22 | 27.08.09 | 18.26 | Tripped due to tripping of associated transmission lines |
|  |  | 06.09.09 | 17.00 | 06.09.09 | 17.14 |  |
|  |  | 13.09.09 | 09.52 | 13.09.09 | 12.00 | Tripped due to tripping of associated transmission lines |
|  |  | 17.09.09 | 10.57 | 17.09.09 | 11.50 |  |
|  |  | 22.09.09 | 10.45 | 22.09.09 | 14.56 | Internal Fault |
|  |  | 03.10.09 | 23.45 | 04.10.09 | 01.29 | Tripped due to tripping of associated transmission lines |
|  |  | 11.10.09 | 12.09 | 11.10.09 | 15.00 | Internal Fault |
|  |  | 23.10.09 | 00.00 | 30.10.09 | 18.35 | Maintenance Work |
|  |  | 31.10.09 | 12.22 | 31.10.09 | 13.50 | Tripped due to tripping of associated transmission lines |
|  |  | 04.11.09 | 08.55 | 04.11.09 | 15.48 |  |
|  |  | 04.11.09 | 19.50 | 04.11.09 | 20.35 |  |
|  |  | 14.12.09 | 16.12 | 16.12.09 | 01.08 | Rotor tripped on E/F |
|  |  | 27.12.09 | 13.44 | 27.12.09 | 15.08 | Internal Fault |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 104 | 02.01.10 | 04.14 | 04.01.10 | 05.10 | Tripping of lines in Northern Region due to fog |
|  |  | 02.01.10 | 05.40 | 02.01.10 | 08.30 |  |
|  |  | 02.01.10 | 21.45 | 02.01.10 | 23.05 |  |
|  |  | 11.01.10 | 15.59 | 11.01.10 | 16.47 |  |
|  |  | 22.01.10 | 13.30 | 22.01.10 | 16.05 | Bleed valve problem |
|  |  | 23.01.10 | 12.45 | 23.01.10 | 17.36 | To change the filter |
|  |  | 29.01.10 | 12.12 | 29.01.10 | 12.58 | Internal fault |
|  |  | 06.02.10 | 10.57 | 06.02.10 | 11.26 | Tripped due to tripping of associated transmission lines |
|  |  | 14.02.10 | 17.37 | 16.02.10 | 00.11 | Internal fault |
|  |  | 26.02.10 | 13.00 | 26.02.10 | 14.14 | Air inlet problem |
| 2 | 104 | 19.04.09 | 10.29 | 19.04.09 | 11.27 | Tripped due to tripping of associated transmission lines |
|  |  | 19.05.09 | 20.55 | 19.05.09 | 22.07 |  |
|  |  | 22.05.09 | 14.39 | 22.05.09 | 14.28 |  |
|  |  | 22.05.09 | 15.36 | 22.05.09 | 15.51 | Tripped due to tripping of associated transmission lines |
|  |  | 01.06.09 | 09.26 | 01.06.09 | 09.52 |  |
|  |  | 04.06.09 | 00.00 | 05.06.09 | 05.26 | Shut-down |
|  |  | 05.06.09 | 15.06 | 05.06.09 | 17.21 | Tripped due to tripping of associated transmission lines |
|  |  | 15.06.09 | 13.35 | 15.06.09 | 14.20 |  |
|  |  | 15.07.09 | 00.30 | 17.08.09 | 19.50 | Shut-down. |
|  |  | 17.08.09 | 23.54 | 18.08.09 | 04.00 | Tripped due to tripping of associated transmission lines |
|  |  | 21.08.09 | 14.42 | 21.08.09 | 15.27 |  |
|  |  | 27.08.09 | 17.53 | 27.08.09 | 19.18 |  |
|  |  | 01.09.09 | 05.05 | 01.09.09 | 05.52 |  |
|  |  | 02.09.09 | 10.17 | 02.09.09 | 11.41 |  |
|  |  | 08.09.09 | 12.05 | 08.09.09 | 13.25 | Internal fault |
|  |  | 13.09.09 | 09.52 | 13.09.09 | 11.26 | Tripped due to tripping of associated transmission lines |
|  |  | 13.09.09 | 18.30 | 13.09.09 | 19.52 | Internal fault |
|  |  | 17.09.09 | 10.57 | 17.09.09 | 12.34 | Tripped due to tripping of associated transmission lines |
|  |  | 18.09.09 | 02.47 | 18.09.09 | 04.20 |  |
|  |  | 19.09.09 | 10.22 | 19.09.09 | 11.26 |  |
|  |  | 28.09.09 | 07.39 | 28.09.09 | 08.30 |  |
|  |  | 02.10.09 | 10.29 | 02.10.09 | 12.21 |  |
|  |  | 11.10.09 | 12.07 | 11.10.09 | 13.38 | Internal Fault |
|  |  | 30.10.09 | 15.12 | 30.10.09 | 15.47 | Transient Fault |
|  |  | 04.11.09 | 19.50 | 04.11.09 | 20.58 | Tripped due to tripping of associated transmission lines |
|  |  | 16.11.09 | 18.14 | 16.11.09 | 19.30 |  |
|  |  | 14.01.10 | 17.13 | 15.01.10 | 11.16 | Internal fault |
|  |  | 05.02.10 | 16.02 | 05.02.10 | 18.00 | Tripped due to tripping of associated transmission lines |
|  |  | 16.02.10 | 10.46 | 18.02.10 | 18.14 | Shut-down for over-hauling of SF6 breaker at IP Ext. end. |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| STG | 122 | 07.04.09 | 06.34 | 07.04.09 | 07.45 | Tripped due to tripping of associated transmission lines |
|  |  | 19.04.09 | 10.29 | 19.04.09 | 12.41 |  |
|  |  | 26.04.09 | 07.11 | 28.04.09 | 13.25 |  |
|  |  | 16.05.09 | 18.44 | 16.05.09 | 20.24 |  |
|  |  | 19.05.09 | 20.55 | 19.05.09 | 23.20 |  |
|  |  | 22.05.09 | 14.39 | 22.05.09 | 15.39 |  |
|  |  | 01.06.09 | 09.26 | 01.06.09 | 10.41 |  |
|  |  | 04.06.09 | 11.25 | 04.06.09 | 15.32 | Oil leakage from ESU |
|  |  | 05.06.09 | 15.06 | 05.06.09 | 16.40 | Tripped due to tripping of associated transmission lines |
|  |  | 15.06.09 | 13.35 | 15.06.09 | 15.20 |  |
|  |  | 14.07.09 | 09.42 | 14.07.09 | 10.42 |  |
|  |  | 15.07.09 | 11.56 | 15.07.09 | 12.50 | Problem in Boiler feed pump |
|  |  | 10.08.09 | 19.10 | 10.08.09 | 20.14 | Tripped due to tripping of associated transmission lines |
|  |  | 12.08.09 | 15.15 | 12.08.09 | 17.20 |  |
|  |  | 18.08.09 | 00.15 | 18.08.09 | 01.55 | Internal Fault |
|  |  | 21.08.09 | 14.43 | 21.08.09 | 16.17 | Tripped due to tripping of associated transmission lines |
|  |  | 27.08.09 | 17.53 | 27.08.09 | 20.20 |  |
|  |  | 11.10.09 | 12.07 | 11.10.09 | 15.06 | Internal Fault |
|  |  | 30.10.09 | 15.12 | 30.10.09 | 16.55 | Internal Fault |
|  |  | 02.01.10 | 04.14 | 02.01.10 | 07.52 | Tripping of lines in Northern Region due to fog |
|  |  | 02.01.10 | 21.45 | 03.01.10 | 00.01 |  |
|  |  | 11.01.10 | 15.59 | 11.01.10 | 16.39 |  |
|  |  | 26.01.10 | 17.56 | 28.01.10 | 16.51 | Excitation problem |
|  |  | 29.01.10 | 12.12 | 29.01.10 | 14.48 | Internal fault |
|  |  | 05.02.10 | 10.50 | 06.02.10 | 12.00 | Vibration in Generator Bearing |
|  |  | 06.02.10 | 10.37 | 06.02.10 | 12.48 | Tripped due to tripping of associated transmission lines |
|  |  | 09.02.10 | 12.55 | 09.02.10 | 14.08 | Internal fault |
|  |  | 14.02.10 | 17.37 | 14.02.10 | 20.09 | Tripped due to tripping of associated transmission lines |

(E)   	BADARPUR THERMAL POWER STATION

| Unit | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 1 | 95 | 30.07.09 | 06.45 | 14.09.09 | 17.00 | Planned shut-down for major overhauling |
|  |  | 22.09.09 | 21.14 | 23.09.09 | 04.08 | Vacuum problem |
|  |  | 23.09.09 | 04.15 | 23.09.09 | 07.02 | Vacuum problem |
|  |  | 26.09.09 | 17.18 | 27.09.09 | 10.40 | Drum main hole leakage |
| 2 | 95 | 10.05.09 | 13.12 | 10.05.09 | 15.15 | Bus differential operated |
|  |  | 16.07.09 | 17.42 | 18.07.09 | 05.25 | Boiler Tube Leakage |
|  |  | 29.07.09 | 17.56 | 30.07.09 | 22.30 | Furnace Failure |
|  |  | 11.08.09 | 21.29 | 11.08.09 | 22.50 | Furnace problem |
|  |  | 30.08.09 | 14.50 | 31.08.09 | 11.00 | DC Control failure |
|  |  | 22.10.09 | 21.48 | 28.12.09 | 05.16 | Annual maintenance |
|  |  | 11.02.10 | 20.10 | 12.02.10 | 08.40 | Reserver shut-down |
|  |  | 21.03.10 | 06.44 | 22.03.10 | 15.05 | PFA fan problem |

| Unit No | Capacity in MW | Outage | Synchronization | Reason of Outage |
| --- | --- | --- | --- | --- |
|  |  | Date | Time | Date | Time |  |
| 3 | 95 | 12.04.09 | 05.34 | 12.04.09 | 19.43 | Electrical problem |
|  |  | 13.04.09 | 17.22 | 13.04.09 | 20.45 | Electrical problem |
|  |  | 25.04.09 | 22.43 | 27.04.09 | 22.47 | Planned Shut-down |
|  |  | 26.05.09 | 20.54 | 27.05.09 | 17.45 | Boiler Tube Leakage |
|  |  | 01.09.09 | 08.40 | 02.09.09 | 15.37 | Boiler Tube Leakage |
|  |  | 30.10.09 | 11.15 | 30.10.09 | 13.04 | Auxiliary supply failed |
|  |  | 16.12.09 | 06.58 | 17.12.09 | 11.65 | Drum level low |
|  |  | 03.02.10 | 13.33 | 04.0210 | 14.05 | Boiler Tube Leakage |
|  |  | 26.02.10 | 2105 | 27.02.10 | 09.30 | Boiler Tube Leakage |
|  |  | 10.03.10 | 22.12 | 11.03.10 | 20.41 | Boiler Tube Leakage |
| 4 | 210 | 01.04.09 | 12.18 | 17.04.09 | 23.59 | Planned Shut-Down for over-hauling |
|  |  | 18.04.09 | 12.35 | 18.04.09 | 15.48 | Tripped along with tripping of 220kV BTPS – Noida Ckt. |
|  |  | 18.05.09 | 13.12 | 10.05.09 | 22.13 | Bus differential operated |
|  |  | 10.06.09 | 16.44 | 11.06.09 | 16.58 | Boiler Tube Leakage |
|  |  | 19.06.09 | 09.52 | 20.06.09 | 09.23 | Boiler Tube Leakage |
|  |  | 11.10.09 | 20.18 | 13.10.09 | 13.09.09 | Boiler Tube Leakage |
|  |  | 24.10.09 | 10.03 | 25.10.09 | 05.51 | Boiler Tube Leakage |
|  |  | 16.11.09 | 14.58 | 17.11.09 | 09.54 | Shut-down |
|  |  | 29.11.09 | 06.43 | 29.11.09 | 23.32 | Boiler Tube leakage |
|  |  | 05.12.09 | 04.54 | 05.12.09 | 12.04 | Electrical Problem |
|  |  | 12.12.09 | 19.25 | 14.12.09 | 16.25 | Boiler Tube leakage |
|  |  | 20.12.09 | 18.35 | 22.12.09 | 09.58 | Boiler Tube leakage |
|  |  | 26.01.10 | 00.05 | 27.01.10 | 09.38 | Reserve shut-down |
|  |  | 02.02.10 | 16.00 | 02.02.10 | 17.55 | Electrical fault |
|  |  | 24.02.10 | 07.22 | 26.02.10 | 08.35 | Boiler Tube Leakage |
|  |  | 03.03.10 | 12.36 | 04.03.10 | 03.40 | Boiler Tube Leakage |
|  |  | 04.03.10 | 12.52 | 05.03.10 | 04.59 | Boiler Tube Leakage |
|  |  | 10.03.10 | 02.27 | 10.03.10 | 21.24 | Boiler Tube Leakage |
|  |  | 12.03.10 | 07.45 | 13.03.10 | 09.11 | Boiler Tube Leakage |
|  |  | 14.03.10 | 23.56 | 15.03.10 | 22.30 | Boiler Tube Leakage |
|  |  | 17.03.10 | 17.35 | 18.03.10 | 22.52 | Boiler Tube Leakage |
|  |  | 21.03.10 | 16.52 | 22.03.10 | 10.45 | Furnace Pressure High |
| 5 | 210 | 07.08.09 | 17.43 | 07.08.09 | 19.40 | Furnace Protection. |
|  |  | 18.11.09 | 00.50 | 19.11.09 | 10.38 | Boiler Tube Leakage |
|  |  | 12.12.09 | 14.35 | 15.12.09 | 19.35 | Boiler Tube leakage |
|  |  | 01.01.10 | 13.08 | 03.01.10 | 07.15 | Boiler Tube leakage |
|  |  | 11.01.10 | 07.38 | 13.01.10 | 23.10 | Boiler Tube leakage |
|  |  | 29.01.10 | 06.20 | 22.03.10 | 18.35 | Annual maintenance |

4	ALLOCATION OF POWER TO DELHI

A)	Allocation from Central Sector Generating Stations to Delhi w.e.f. 01.03.2010

i) TIME BLOCK -  00.00hrs & 18.00hrs. and 23.00-24.00hrs @ 0% from unallocated quota of Central Sector Generating Stations

All figures in MW

| Name of the Stn | Installed capacity | Total Un- allocated | Basic Allocation | Basic Allocation at periphery | Allocation out of Unallocated Quota | Allocation out of Un-allocation Quota at Delhi periphery | Total allocation at Delhi periphery |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | (8)=(5)+(7) |
| NTPC STATIONS |  |  |  |  |  |  |  |
| Singrauli STPS | 2000 | 300 | 150 | 130 | 0 | 0 | 130 |
| Rihand | 1000 | 150 | 100 | 87 | 0 | 0 | 87 |
| Rihand Stage -II | 1000 | 150 | 126 | 109 | 0 | 0 | 109 |
| ANTA GPS | 419 | 63 | 44 | 41 | 0 | 0 | 41 |
| Auriya GPS | 663.36 | 99 | 72 | 67 | 0 | 0 | 67 |
| Dadri GPS | 829.78 | 129 | 91 | 85 | 0 | 0 | 85 |
| Dadri NCTPS (Th) | 840 | 0 | 756 | 657 | 0 | 0 | 657 |
| Dadri NCTPS (Th) Stage-II | 490 | 0 | 441 | 383 | 0 | 0 | 383 |
| Unchahaar-I TPS | 420 | 20 | 24 | 21 | 0 | 0 | 21 |
| Unchahaar-II TPS | 420 | 63 | 47 | 41 | 0 | 0 | 41 |
| Unchahaar-III TPS | 210 | 31 | 29 | 25 | 0 | 0 | 25 |
| TOTAL | 8292 | 1005 | 1880 | 1646 | 0 | 0 | 1646 |
| NHPC |  |  |  |  |  |  |  |
| Baira Suil HPS | 180 | 0 | 20 | 19 | 0 | 0 | 19 |
| Salal HPS | 690 | 0 | 80 | 76 | 0 | 0 | 76 |
| Tanakpur HEP | 94 | 0 | 12 | 11 | 0 | 0 | 11 |
| Chamera HEP | 540 | 0 | 43 | 41 | 0 | 0 | 41 |
| Chamera-II HEP | 300 | 54 | 40 | 38 | 0 | 0 | 38 |
| URI HEP | 480 | 0 | 53 | 50 | 0 | 0 | 50 |
| Dhauli Ganga HEP | 280 | 42 | 37 | 35 | 0 | 0 | 35 |
| Dulhasti HEP | 390 | 58 | 50 | 48 | 0 | 0 | 48 |
| TOTAL | 2954 | 154 | 335 | 318 | 0 | 0 | 318 |
| NPC |  |  |  |  |  |  |  |
| Narora APS | 440 | 64 | 47 | 41 | 0 | 0 | 41 |
| RAPP(B) | 440 | 66 | 0 | 0 | 0 | 0 | 0 |
| RAPP (C ) | 220 | 32 | 28 | 24 | 0 | 0 | 24 |
| TOTAL | 1100 | 162 | 75 | 65 | 0 | 0 | 65 |
| SVJNL |  |  |  |  |  |  |  |
| Nathpa Jhakri HEP | 1500 | 149 | 142 | 123 | 0 | 0 | 123 |
| THDC |  |  |  |  |  |  |  |
| Tehri Hydro | 1000 | 99 | 103 | 89 | 0 | 0 | 89 |
| Total | 14846 | 1569 | 2535 | 2242 | 0 | 0 | 2242 |
| Allocation from ER and Tala HEP |  |  |  |  |  |  |  |
| Farakka | 1600 | 0 | 30 | 25 | 0 | 0 | 25 |
| Kahalgaon | 840 | 0 | 63 | 53 | 0 | 0 | 53 |
| Talchar | 1000 | 0 | 0 | 0 | 0 | 0 | 0 |
| Tala HEP | 1020 | 153 | 30 | 25 | 0 | 0 | 25 |
| Mejia TPS Unit-6 | 250 | 0 | 29 | 25 | 0 | 0 | 25 |
| Kahalgaon-II | 1000 | 0 | 108 | 90 | 0 | 0 | 90 |
| Total ER | 5710 | 153 | 260 | 217 | 0 | 0 | 217 |
| Grand Total | 20556 | 1722 | 2795 | 2459 | 0 | 0 | 2459 |

ii) Time Block 18.00hrs. to 23.00hrs. @ 0% allocation from Central Sector Generating Stations and 3.18% from RAPP-B

All figures in MW

| Name of the Stn | Installed capacity | Total Un- allocated | Basic Allocation | Basic Allocation at periphery | Allocation out of Unallocated Quota | Allocation out of Un-allocation Quota at Delhi periphery | Total allocation at Delhi periphery |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | (8)=(5)+(7) |
| NTPC STATIONS |  |  |  |  |  |  |  |
| Singrauli STPS | 2000 | 300 | 150 | 130 | 0 | 0 | 130 |
| Rihand | 1000 | 150 | 100 | 87 | 0 | 0 | 87 |
| Rihand Stage -II | 1000 | 150 | 126 | 109 | 0 | 0 | 109 |
| ANTA GPS | 419 | 63 | 44 | 41 | 0 | 0 | 41 |
| Auriya GPS | 663.36 | 99 | 72 | 67 | 0 | 0 | 67 |
| Dadri GPS | 829.78 | 129 | 91 | 85 | 0 | 0 | 85 |
| Dadri NCTPS (Th) | 840 | 0 | 756 | 657 | 0 | 0 | 657 |
| Dadri NCTPS (Th) Stage-II | 490 | 0 | 441 | 383 | 0 | 0 | 383 |
| Unchahaar-I TPS | 420 | 20 | 24 | 21 | 0 | 0 | 21 |
| Unchahaar-II TPS | 420 | 63 | 47 | 41 | 0 | 0 | 41 |
| Unchahaar-III TPS | 210 | 31 | 29 | 25 | 0 | 0 | 25 |
| TOTAL | 8292 | 1005 | 1880 | 1646 | 0 | 0 | 1646 |
| NHPC |  |  |  |  |  |  |  |
| Baira Suil HPS | 180 | 0 | 20 | 19 | 0 | 0 | 19 |
| Salal HPS | 690 | 0 | 80 | 76 | 0 | 0 | 76 |
| Tanakpur HEP | 94 | 0 | 12 | 11 | 0 | 0 | 11 |
| Chamera HEP | 540 | 0 | 43 | 41 | 0 | 0 | 41 |
| Chamera-II HEP | 300 | 54 | 40 | 38 | 0 | 0 | 38 |
| URI HEP | 480 | 0 | 53 | 50 | 0 | 0 | 50 |
| Dhauli Ganga HEP | 280 | 42 | 37 | 35 | 0 | 0 | 35 |
| Dulhasti HEP | 390 | 58 | 50 | 48 | 0 | 0 | 48 |
| TOTAL | 2954 | 154 | 335 | 318 | 0 | 0 | 318 |
| NPC |  |  |  |  |  |  |  |
| Narora APS | 440 | 64 | 47 | 41 | 0 | 0 | 41 |
| RAPP(B) | 440 | 66 | 0 | 0 | 14 | 12 | 12 |
| RAPP (C ) | 220 | 32 | 28 | 24 | 0 | 0 | 24 |
| TOTAL | 1100 | 162 | 75 | 65 | 14 | 12 | 77 |
| SVJNL |  |  |  |  |  |  |  |
| Nathpa Jhakri HEP | 1500 | 149 | 142 | 123 | 0 | 0 | 123 |
| THDC |  |  |  |  |  |  |  |
| Tehri Hydro | 1000 | 99 | 103 | 89 | 0 | 0 | 89 |
| Total | 14846 | 1569 | 2535 | 2242 | 14 | 12 | 2254 |
| Allocation from ER and Tala HEP |  |  |  |  |  |  |  |
| Farakka | 1600 | 0 | 30 | 25 | 0 | 0 | 25 |
| Kahalgaon | 840 | 0 | 63 | 53 | 0 | 0 | 53 |
| Talchar | 1000 | 0 | 0 | 0 | 0 | 0 | 0 |
| Tala HEP | 1020 | 153 | 30 | 25 | 0 | 0 | 25 |
| Mejia TPS Unit-6 | 250 | 0 | 29 | 25 | 0 | 0 | 25 |
| Kahalgaon-II | 1000 | 0 | 108 | 90 | 0 | 0 | 90 |
| Total ER | 5710 | 153 | 260 | 217 | 0 | 0 | 217 |
| Grand Total | 20556 | 1722 | 2795 | 2459 | 14 | 12 | 2471 |

5	ALLOCATION OF POWER TO VARIOUS LISCENCEES AS PER ORDER OF DERC AND DECISION OF GNCTD FOR ALLOCATION OF CENTRAL SECTOR STATIONS (EXCEPT DADRI THERMAL AND BTPS) AND STATE SECTOR GENERATING STATIONS w.e.f. 01.07.2009.

(Allocation In % )

i)	Allocation during the period 00.00 - 10.00hrs. and 17.00 - 24.00hrs.

| SOURCES | LICENSEES |
| --- | --- |
|  | NDMC | MES | NDPL | BRPL | BYPL | TOTAL |
| 1. Central Sector without Dadri (Th) | 00.00 | 00.00 | 29.18 | 43.58 | 27.24 | 100.00 |
| 2. Dadri (Th) | 14.05 | 00.00 | 23.89 | 36.36 | 27.70 | 100.00 |
| 3. BTPS | 15.07 | 7.09 | 21.61 | 32.90 | 23.33 | 100.00 |
| 4. IP | 00.00 | 00.00 | 28.02 | 42.51 | 29.47 | 100.00 |
| 5. RPH | 00.00 | 00.00 | 27.99 | 42.48 | 29.53 | 100.00 |
| 6. GT | 00.00 | 00.00 | 27.99 | 42.48 | 29.53 | 100.00 |
| 7. Pragati | 25.76 | 00.00 | 20.47 | 31.26 | 22.51 | 100.00 |

ii)	Allocation during the period 10.00 - 17.00hrs.

| SOURCES | LICENSEES |
| --- | --- |
|  | NDMC | MES | NDPL | BRPL | BYPL | TOTAL |
| 1. Central Sector without Dadri (Th) | 00.00 | 00.00 | 29.18 | 43.58 | 27.24 | 100.00 |
| 2. Dadri (Th) | 14.91 | 00.00 | 23.89 | 35.50 | 25.70 | 100.00 |
| 3. BTPS | 15.87 | 7.09 | 21.61 | 32.10 | 23.33 | 100.00 |
| 4. IP | 00.83 | 00.00 | 28.02 | 41.68 | 29.47 | 100.00 |
| 5. RPH | 00.86 | 00.00 | 27.99 | 41.62 | 29.53 | 100.00 |
| 6. GT | 00.86 | 00.00 | 27.99 | 41.62 | 29.53 | 100.00 |
| 7. Pragati | 26.61 | 00.00 | 20.47 | 30.41 | 22.51 | 100.00 |

6	POWER AVAILABILITY-DEMAND POSITION AT THE TIME OF PEAK DEMAND MET DURING MARCH 2010

All figures in MW

| Date | Time of peak demand | Generation within Delhi | Import from the Grid | Schedule from the Grid | OD(-) / UD(+) | Demand met | Shedding | Un-Restricted Demand |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | IP | RPH | GT | PPCL | BTPS | Total |  |  |  |  |  |  |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8)= (3) to (7) | (9) | (10) | (11)= (10) -(9) | (12)= (10)+ (11) | (13) | (14)= (12)+ (13) |
| 1 | 19:33:47 | 0 | 101 | 144 | 271 | 349 | 865 | 1224 | 2285 | 1061 | 2089 | 17 | 2106 |
| 2 | 19:16:43 | 0 | 113 | 146 | 310 | 389 | 958 | 1571 | 2040 | 469 | 2529 | 0 | 2529 |
| 3 | 19:19:37 | 0 | 115 | 174 | 309 | 221 | 819 | 1961 | 2126 | 165 | 2780 | 9 | 2789 |
| 4 | 19:19:05 | 0 | 113 | 168 | 303 | 339 | 923 | 2065 | 1659 | -406 | 2988 | 0 | 2988 |
| 5 | 19:18:04 | 0 | 111 | 146 | 307 | 419 | 983 | 1888 | 2128 | 240 | 2871 | 0 | 2871 |
| 6 | 19:09:05 | 0 | 113 | 176 | 305 | 433 | 1027 | 1743 | 2127 | 384 | 2770 | 0 | 2770 |
| 7 | 19:30:00 | 0 | 0 | 166 | 311 | 398 | 875 | 1658 | 2371 | 713 | 2533 | 0 | 2533 |
| 8 | 19:08:58 | 0 | 112 | 141 | 314 | 427 | 994 | 1728 | 2357 | 629 | 2722 | 0 | 2722 |
| 9 | 19:17:22 | 0 | 112 | 142 | 312 | 442 | 1008 | 1794 | 1933 | 139 | 2802 | 0 | 2802 |
| 10 | 19:25:11 | 0 | 111 | 181 | 311 | 208 | 811 | 1991 | 1857 | -134 | 2802 | 0 | 2802 |
| 11 | 19:17:38 | 0 | 111 | 164 | 307 | 347 | 929 | 1955 | 2057 | 102 | 2884 | 0 | 2884 |
| 12 | 19:27:46 | 0 | 113 | 160 | 310 | 242 | 825 | 2110 | 2237 | 127 | 2935 | 3 | 2938 |
| 13 | 19:17:16 | 0 | 109 | 124 | 306 | 427 | 966 | 1876 | 2158 | 282 | 2842 | 0 | 2842 |
| 14 | 19:19:57 | 0 | 113 | 137 | 304 | 426 | 980 | 1692 | 2301 | 609 | 2672 | 0 | 2672 |
| 15 | 19:20:17 | 0 | 113 | 136 | 300 | 231 | 780 | 2142 | 2141 | -1 | 2922 | 0 | 2922 |
| 16 | 19:19:54 | 0 | 110 | 146 | 301 | 399 | 956 | 2033 | 2015 | -18 | 2989 | 6 | 2995 |
| 17 | 19:21:24 | 0 | 112 | 145 | 297 | 228 | 782 | 2042 | 1824 | -218 | 2824 | 197 | 3021 |
| 18 | 19:05:05 | 0 | 110 | 146 | 302 | 226 | 784 | 2349 | 2123 | -226 | 3133 | 0 | 3133 |
| 19 | 19:21:34 | 0 | 111 | 146 | 298 | 412 | 967 | 2210 | 2239 | 29 | 3177 | 0 | 3177 |
| 20 | 19:17:10 | 0 | 113 | 145 | 294 | 400 | 952 | 2165 | 2154 | -11 | 3117 | 7 | 3124 |
| 21 | 19:50:25 | 0 | 53 | 145 | 293 | 121 | 612 | 2323 | 2312 | -11 | 2935 | 0 | 2935 |
| 22 | 19:19:03 | 0 | 113 | 174 | 290 | 403 | 980 | 2321 | 2234 | -87 | 3301 | 0 | 3301 |
| 23 | 19:18:59 | 0 | 108 | 180 | 290 | 569 | 1147 | 2125 | 2180 | 55 | 3272 | 0 | 3272 |
| 24 | 19:17:24 | 0 | 60 | 175 | 289 | 605 | 1129 | 2135 | 2217 | 82 | 3264 | 0 | 3264 |
| 25 | 19:02:12 | 0 | 114 | 181 | 292 | 598 | 1185 | 2179 | 2287 | 108 | 3364 | 2 | 3366 |
| 26 | 19:20:11 | 0 | 111 | 178 | 288 | 598 | 1175 | 2236 | 2235 | -1 | 3411 | 0 | 3411 |
| 27 | 19:20:56 | 0 | 111 | 176 | 290 | 587 | 1164 | 2091 | 2200 | 109 | 3255 | 0 | 3255 |
| 28 | 19:35:39 | 0 | 112 | 172 | 294 | 571 | 1149 | 1863 | 2273 | 410 | 3012 | 0 | 3012 |
| 29 | 19:52:07 | 0 | 109 | 132 | 290 | 600 | 1131 | 2181 | 2277 | 96 | 3312 | 0 | 3312 |
| 30 | 19:43:22 | 0 | 52 | 176 | 289 | 595 | 1112 | 2295 | 2273 | -22 | 3407 | 0 | 3407 |
| 31 | 19:18:14 | 0 | 112 | 180 | 290 | 584 | 1166 | 2240 | 2480 | 240 | 3406 | 0 | 3406 |

7	POWER AVAILABILITY- DEMAND POSITION AT THE TIME OF MAXIMUM UNRESTRICTED DEMAND DURING MARCH 2010

All figures in MW

| Date | Time of peak demand | Generation within Delhi | Import from the Grid | Schedule from the Grid | OD(-) / UD(+) | Demand met | Shedding | Un-Restricted Demand |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | IP | RPH | GT | PPCL | BTPS | Total |  |  |  |  |  |  |
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8)=(3) to (7) | (9) | (10) | (11)= (10) -(9) | (12)=(10) + (11) | (13) | (14)= (12)+ (13) |
| 1 | 19:33:47 | 0 | 101 | 144 | 271 | 349 | 865 | 1224 | 2285 | 1061 | 2089 | 17 | 2106 |
| 2 | 19:16:43 | 0 | 113 | 146 | 310 | 389 | 958 | 1571 | 2040 | 469 | 2529 | 0 | 2529 |
| 3 | 19:19:37 | 0 | 115 | 174 | 309 | 221 | 819 | 1961 | 2126 | 165 | 2780 | 9 | 2789 |
| 4 | 19:19:05 | 0 | 113 | 168 | 303 | 339 | 923 | 2065 | 1659 | -406 | 2988 | 0 | 2988 |
| 5 | 19:18:04 | 0 | 111 | 146 | 307 | 419 | 983 | 1888 | 2128 | 240 | 2871 | 0 | 2871 |
| 6 | 19:09:05 | 0 | 113 | 176 | 305 | 433 | 1027 | 1743 | 2127 | 384 | 2770 | 0 | 2770 |
| 7 | 19:30:00 | 0 | 0 | 166 | 311 | 398 | 875 | 1658 | 2371 | 713 | 2533 | 0 | 2533 |
| 8 | 19:08:58 | 0 | 112 | 141 | 314 | 427 | 994 | 1728 | 2357 | 629 | 2722 | 0 | 2722 |
| 9 | 19:17:22 | 0 | 112 | 142 | 312 | 442 | 1008 | 1794 | 1933 | 139 | 2802 | 0 | 2802 |
| 10 | 19:25:11 | 0 | 111 | 181 | 311 | 208 | 811 | 1991 | 1857 | -134 | 2802 | 0 | 2802 |
| 11 | 19:17:38 | 0 | 111 | 164 | 307 | 347 | 929 | 1955 | 2057 | 102 | 2884 | 0 | 2884 |
| 12 | 19:27:46 | 0 | 113 | 160 | 310 | 242 | 825 | 2110 | 2237 | 127 | 2935 | 3 | 2938 |
| 13 | 19:17:16 | 0 | 109 | 124 | 306 | 427 | 966 | 1876 | 2158 | 282 | 2842 | 0 | 2842 |
| 14 | 19:19:57 | 0 | 113 | 137 | 304 | 426 | 980 | 1692 | 2301 | 609 | 2672 | 0 | 2672 |
| 15 | 19:20:17 | 0 | 113 | 136 | 300 | 231 | 780 | 2142 | 2141 | -1 | 2922 | 0 | 2922 |
| 16 | 19:19:54 | 0 | 110 | 146 | 301 | 399 | 956 | 2033 | 2015 | -18 | 2989 | 6 | 2995 |
| 17 | 19:21:24 | 0 | 112 | 145 | 297 | 228 | 782 | 2042 | 1824 | -218 | 2824 | 197 | 3021 |
| 18 | 19:05:05 | 0 | 110 | 146 | 302 | 226 | 784 | 2349 | 2123 | -226 | 3133 | 0 | 3133 |
| 19 | 19:21:34 | 0 | 111 | 146 | 298 | 412 | 967 | 2210 | 2239 | 29 | 3177 | 0 | 3177 |
| 20 | 19:17:10 | 0 | 113 | 145 | 294 | 400 | 952 | 2165 | 2154 | -11 | 3117 | 7 | 3124 |
| 21 | 19:50:25 | 0 | 53 | 145 | 293 | 121 | 612 | 2323 | 2312 | -11 | 2935 | 0 | 2935 |
| 22 | 19:19:03 | 0 | 113 | 174 | 290 | 403 | 980 | 2321 | 2234 | -87 | 3301 | 0 | 3301 |
| 23 | 19:18:59 | 0 | 108 | 180 | 290 | 569 | 1147 | 2125 | 2180 | 55 | 3272 | 0 | 3272 |
| 24 | 19:17:24 | 0 | 60 | 175 | 289 | 605 | 1129 | 2135 | 2217 | 82 | 3264 | 0 | 3264 |
| 25 | 19:02:12 | 0 | 114 | 181 | 292 | 598 | 1185 | 2179 | 2287 | 108 | 3364 | 2 | 3366 |
| 26 | 19:20:11 | 0 | 111 | 178 | 288 | 598 | 1175 | 2236 | 2235 | -1 | 3411 | 0 | 3411 |
| 27 | 19:20:56 | 0 | 111 | 176 | 290 | 587 | 1164 | 2091 | 2200 | 109 | 3255 | 0 | 3255 |
| 28 | 19:35:39 | 0 | 112 | 172 | 294 | 571 | 1149 | 1863 | 2273 | 410 | 3012 | 0 | 3012 |
| 29 | 19:52:07 | 0 | 109 | 132 | 290 | 600 | 1131 | 2181 | 2277 | 96 | 3312 | 0 | 3312 |
| 30 | 19:43:22 | 0 | 52 | 176 | 289 | 595 | 1112 | 2295 | 2273 | -22 | 3407 | 0 | 3407 |
| 31 | 19:18:14 | 0 | 112 | 180 | 290 | 584 | 1166 | 2240 | 2480 | 240 | 3406 | 0 | 3406 |

8 	SOURCEWISE SCHEDULED DRAWL FROM NORTHERN GRID AS WELL AS

AVAILABILITY WITHIN DELHI FOR MARCH 2010

A)   AVAILABILITY FROM GENCO AND PRAGATI STNs. (all fig in MUs)

| A (i) RPH | 85.164 |
| --- | --- |
| JHAJJAR SHARE | 0.682 |
| NET RPH | 84.482 |
| (ii) GT+WHRU | 117.470 |
| (iii) PRAGATI | 230.136 |
| TOTAL (i+ii+iii) | 432.088 |
| B) AVAILABILITY FROM BTPS | 326.127 |
| C) AUXILIARY CONSUMPTION OF GENERATING STNs. EXCLUDING BTPS | 19.799 |
| D) NET GENERATION AVAILABLE WITHIN DELHI(A+B-C) | 738.416 |

B)  SOURCE WISE SCHEDULED DRAWL FROM THE NORTHERN GRID

| NAME OF THE STATION | AVAILABILITY AT POWER PLANT | AVAILABILITY AT DELHI PERIPHERY | ALLOCATION MADE BY NRLDC AT POWER PLANT | ALLOCATION MADE BY NRLDC AT DELHI PERIPHERY |
| --- | --- | --- | --- | --- |
| BAIRA-SUIL | 8.380 | 8.080 | 8.380 | 8.080 |
| SALAL | 22.576 | 21.767 | 20.645 | 19.903 |
| TANAKPUR | 2.193 | 2.114 | 2.159 | 2.081 |
| CHAMERA | 10.748 | 10.364 | 10.748 | 10.364 |
| CHAMERA-II | 9.498 | 9.159 | 9.498 | 9.159 |
| DHAULI GANGA | 5.551 | 5.353 | 5.551 | 5.353 |
| SINGRAULI | 107.904 | 104.006 | 107.613 | 103.726 |
| URI | 36.773 | 35.444 | 37.013 | 35.675 |
| ANTA (GAS) | 18.869 | 18.190 | 18.836 | 18.158 |
| ANTA (RLNG) | 11.491 | 11.072 | 5.044 | 4.867 |
| RIHAND-I | 67.378 | 64.944 | 67.191 | 64.765 |
| RIHAND-II | 89.702 | 86.469 | 89.480 | 86.256 |
| AURAIYA (GAS) | 31.538 | 30.392 | 31.480 | 30.336 |
| AURAIYA (LIQUID) | 0.592 | 0.568 | 0.007 | 0.007 |
| AURAIYA (RLNG) | 10.484 | 10.102 | 4.208 | 4.060 |
| DADRI(GT) (GAS) | 43.550 | 41.981 | 43.489 | 41.922 |
| DADRI(GT) (LIQUID) | 4.305 | 4.151 | 0.199 | 0.192 |
| DADRI(GT) (RLNG) | 14.829 | 14.285 | 6.039 | 5.824 |
| UNCHAHAR-I | 17.041 | 16.425 | 16.332 | 15.745 |
| UNCHAHAR-III | 20.107 | 19.381 | 19.246 | 18.555 |
| DADRI(TH) | 535.623 | 516.267 | 527.913 | 508.866 |
| UNCHAHAR-II | 33.381 | 32.177 | 32.030 | 30.878 |
| NAPP | 9.162 | 8.833 | 9.162 | 8.833 |
| RAPP-B | 1.292 | 1.245 | 1.292 | 1.245 |
| RAPP-C | 17.930 | 17.283 | 17.930 | 17.283 |
| GUJRAT | 14.837 | 13.971 | 13.377 | 12.893 |
| GUJRAT | 7.451 | 7.017 | 7.017 | 6.766 |
| HIMACHAL PRADESH | 0.442 | 0.424 | 0.442 | 0.424 |
| TO MEGHALAYA | -8.629 | -8.830 | -8.830 | -9.161 |
| TO ANDHRA PRADESH | -44.291 | -45.345 | -45.345 | -47.072 |
| TO ANDHRA PRADESH | -3.840 | -4.072 | -4.072 | -4.216 |
| MADHYA PRADESH | 0.620 | 0.586 | 0.586 | 0.567 |
| CHHATTISGARH | 0.360 | 0.340 | 0.340 | 0.329 |
| TO HARYANA | -6.409 | -6.639 | -6.409 | -6.639 |
| DVC | 30.387 | 29.691 | 29.691 | 28.617 |
| MAHARASHTRA | 10.361 | 9.761 | 9.288 | 8.960 |
| CHHATTISGARH | 71.705 | 67.531 | 64.154 | 61.859 |

| NAME OF THE STATION | AVAILABILITY AT POWER PLANT | AVAILABILITY AT DELHI PERIPHERY | ALLOCATION MADE BY NRLDC AT POWER PLANT | ALLOCATION MADE BY NRLDC AT DELHI PERIPHERY |
| --- | --- | --- | --- | --- |
| TO RAJASTHAN | -5.929 | -6.146 | -5.929 | -6.146 |
| TO TAMILNADU | -15.915 | -16.290 | -16.290 | -16.903 |
| PUNJAB | 18.527 | 16.678 | 16.678 | 16.076 |
| TO MADHYA PRADESH | -12.003 | -12.751 | -12.751 | -13.238 |
| MADHYA PRADESH | 1.662 | 1.565 | 1.491 | 1.438 |
| ANDHRA PRADESH | 10.074 | 9.445 | 9.228 | 8.895 |
| TO MAHARASHTRA | -10.734 | -11.400 | -11.400 | -11.827 |
| TO UTTAR PRADESH | -0.662 | -0.690 | -0.662 | -0.690 |
| TO WEST BENGAL | -23.006 | -23.545 | -23.545 | -24.428 |
| RAJASTHAN | 7.457 | 6.882 | 6.882 | 6.644 |
| TO HIMACHAL PRADESH | -25.638 | -26.599 | -25.638 | -26.599 |
| TO UTTRANCHAL | -47.091 | -48.856 | -47.091 | -48.856 |
| TO KARNATAKA | -59.041 | -60.460 | -60.460 | -62.773 |
| KARNATAKA | 47.197 | 44.250 | 41.504 | 40.002 |
| TO POWER EXCHANGE (IEX) | -60.700 | -63.082 | -60.700 | -63.082 |
| POWER EXCHANGE (IEX) | 43.143 | 41.649 | 43.143 | 41.649 |
| UNREQUISITIONED SURPLUS | 1.258 | 1.303 | 1.258 | 1.303 |
| POWER EXCHANGE -PX | 0.120 | 0.116 | 0.120 | 0.116 |
| NATHPA JHAKARI | 27.734 | 26.742 | 27.734 | 26.742 |
| DULHASTI | 15.726 | 15.162 | 15.726 | 15.162 |
| TEHRI | 25.115 | 24.206 | 25.115 | 24.206 |
| KAHELGAON-II | 67.304 | 65.773 | 65.018 | 62.681 |
| TALA | 0.878 | 0.858 | 0.858 | 0.828 |
| FARAKKA | 15.081 | 14.733 | 14.591 | 14.058 |
| KAHELGAON-I | 32.427 | 31.674 | 31.303 | 30.161 |
| DADRI (THERMAL)-II | 127.230 | 122.398 | 122.614 | 117.967 |
| TOTAL SCHEDULE FROM THE GRID | 1384.106 | 1308.104 | 1310.519 | 1238.847 |

C)   AGENCY WISE BREAKUP OF ENERGY SCHEDULED DRAWL FROM THE GRID

| NAME OF THE STATION | AVAILABILITY AT POWER PLANT | AVAILABILITY AT PERIPHERY | ALLOCATION MADE BY NRLDC AT POWER PLANT | ALLOCATION MADE BY NRLDC AT POWER PERIPHERY |
| --- | --- | --- | --- | --- |
| NTPC - NR | 1134.023 | 1092.809 | 1091.719 | 1052.123 |
| NTPC -ER | 114.812 | 112.180 | 110.913 | 106.900 |
| NHPC | 111.445 | 107.444 | 109.719 | 105.778 |
| NPC | 28.384 | 27.360 | 28.384 | 27.360 |
| HIMACHAL PRADESH | 0.442 | 0.424 | 0.442 | 0.424 |
| GUJARAT | 14.837 | 13.971 | 13.377 | 12.893 |
| GUJARAT | 7.451 | 7.017 | 7.017 | 6.766 |
| CHHATTISGARH | 0.360 | 0.340 | 0.340 | 0.329 |
| CHHATTISGARH | 71.705 | 67.531 | 64.154 | 61.859 |
| MADHYA PRADESH | 0.620 | 0.586 | 0.586 | 0.567 |
| MADHYA PRADESH | 1.662 | 1.565 | 1.491 | 1.438 |
| ANDHRA PRADESH | 10.074 | 9.445 | 9.228 | 8.895 |
| PUNJAB | 18.527 | 16.678 | 16.678 | 16.076 |
| DVC | 30.387 | 29.691 | 29.691 | 28.617 |
| KARNATAKA | 47.197 | 44.250 | 41.504 | 40.002 |
| RAJASTHANN | 7.457 | 6.882 | 6.882 | 6.644 |
| MAHARASHTRA | 10.361 | 9.761 | 9.288 | 8.960 |
| POWER EXCHANGE (IEX) | 43.143 | 41.649 | 43.143 | 41.649 |
| UNREQUISITIONED SURPLUS | 1.258 | 1.303 | 1.258 | 1.303 |

| NAME OF THE STATION | AVAILABILITY AT POWER PLANT | AVAILABILITY AT DELHI PERIPHERY | ALLOCATION MADE BY NRLDC AT POWER PLANT | ALLOCATION MADE BY NRLDC AT DELHI PERIPHERY |
| --- | --- | --- | --- | --- |
| NATHPA JHAKARI | 27.734 | 26.742 | 27.734 | 26.742 |
| TEHRI | 25.115 | 24.206 | 25.115 | 24.206 |
| TALA | 0.878 | 0.858 | 0.858 | 0.828 |
| POWER EXCHANGE -PX | 0.120 | 0.116 | 0.120 | 0.116 |
| TOTAL SCHEDULE FROM THE GRID | 1707.992 | 1642.809 | 1639.641 | 1580.475 |

D) AGENCY WISE BREAKUP OF ENERGY SCHEDULED BY NRLDC FOR EXPORT TO OTHER UTILITIES FROM DTL

| NAME OF THE STATION | AVAILABILITY AT POWER PLANT | AVAILABILITY AT PERIPHERY | ALLOCATION MADE BY NRLDC AT POWER PLANT | ALLOCATION MADE BY NRLDC AT POWER PERIPHERY |
| --- | --- | --- | --- | --- |
| TO MEGHALAYA | -8.627 | -8.830 | -8.830 | -9.161 |
| TO ANDHRA PRADESH | -44.291 | -45.345 | -45.345 | -47.072 |
| TO ANDHRA PRADESH | -3.840 | -4.072 | -4.072 | -4.216 |
| TO HARYANA | -6.409 | -6.639 | -6.409 | -6.639 |
| TO RAJASTHAN | -5.929 | -6.146 | -5.929 | -6.146 |
| TO TAMIL NADU | -15.915 | -16.290 | -16.290 | -16.903 |
| TO MADHYA PRADESH | -12.003 | -12.751 | -12.751 | -13.238 |
| TO MAHARASHTRA | -10.734 | -11.400 | -11.400 | -11.827 |
| TO UTTAR PRADESH | -0.662 | -0.690 | -0.662 | -0.690 |
| TO WEST BENGAL | -23.006 | -23.545 | -23.545 | -24.428 |
| TO HIMACHAL PRADESH | -25.638 | -26.599 | -25.638 | -26.599 |
| TO UTTRANCHAL | -47.091 | -48.856 | -47.091 | -48.856 |
| TO KARNATAKA | -59.041 | -60.460 | -60.460 | -62.773 |
| TO POWER EXCHANGE (IEX) | -60.700 | -63.082 | -60.700 | -63.082 |
| TOTAL | -323.886 | -334.705 | -329.122 | -341.629 |
| (G) TOTAL SCHEDULED DRAWL FROM THE GRID (G=Fa+Fb+Fc) | 1384.106 | 1308.104 | 1310.519 | 1238.847 |
| TOTAL CONSUMPTION INCLUDING AUX. OF GENERATING STNs. EXCLUDING BTPS | 1760.884 |
| NET CONSUMPTION | 1741.085 |
| AVAILABILITY WITHIN DELHI | 738.416 |
| ACTUAL DRAWAL FROM THE GRID | 1002.669 |
| OVER DRAWAL(+)/UNDER DRAWAL(-) FROM THE GRID ON THE BASIS OF SCHEDULED ALLOCATION MADE BY NRLDC TO DELHI AT PERIPHERY | -236.178 |
| LOAD SHEDDING | 6.446 |
| UNRESTRICTED DEMAND (GROSS) | 1767.330 |
| UNRESTRICTED DEMAND (NET) | 1747.531 |
| MAX. NET CONSUMPTION | 68.935Mus. ON 31.03.2010 |
| MAX. LOAD SHEDDING | 268 MW ON 17.03.2010 AT 19:30HRS. |
| PEAK LOAD DAY PEAK EVENING PEAK | Peak Demand during the month 3268MW AT 12:01HRS ON 31.03.2010 3411MW AT 19.20.11HRS ON 26.03.2010 | SHEDDING AT PEAK TIME 02MW NIL |
| P.L.F. OF GENCO AND PRAGATI STNs. | IP RPH GT PRAGATI | 0.00% 84.79% 58.48% 93.73% |

9	SHEDDING DETAILS DURING THE MONTH OF MARCH 2010.

### ALL FIGURES IN MUs

| DATE | No. of Under Freq. Relay Operated | Shedding due to under frequency relay operation in MUs | Shedding due to Grid Restrictions (Over drawal / low freq.) |
| --- | --- | --- | --- |
|  |  | BSES | NDPL | NDMC | TOTAL | BSES | NDPL | NDMC |
|  |  | BYPL | BRPL |  |  |  | BYPL | BRPL |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7=3 to 6 | 8 | 9 | 10 | 11 |
| 01-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 02-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 03-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 04-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 05-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 06-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 07-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 08-Mar-10 | 1 | 0.000 | 0.003 | 0.000 | 0.000 | 0.003 | 0.000 | 0.000 | 0.000 | 0.000 |
| 09-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 10-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 11-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 12-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 13-Mar-10 | 3 | 0.000 | 0.016 | 0.008 | 0.000 | 0.024 | 0.000 | 0.000 | 0.000 | 0.000 |
| 14-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 15-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 16-Mar-10 | 5 | 0.002 | 0.008 | 0.004 | 0.000 | 0.014 | 0.000 | 0.000 | 0.000 | 0.000 |
| 17-Mar-10 | 3 | 0.001 | 0.000 | 0.011 | 0.000 | 0.012 | 0.447 | 0.418 | 0.183 | 0.000 |
| 18-Mar-10 | 15 | 0.003 | 0.017 | 0.116 | 0.000 | 0.136 | 0.102 | 0.050 | 0.003 | 0.000 |
| 19-Mar-10 | 9 | 0.005 | 0.031 | 0.027 | 0.000 | 0.063 | 0.000 | 0.000 | 0.000 | 0.000 |
| 20-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 21-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 22-Mar-10 | 4 | 0.001 | 0.014 | 0.002 | 0.000 | 0.017 | 0.000 | 0.000 | 0.000 | 0.000 |
| 23-Mar-10 | 3 | 0.000 | 0.005 | 0.002 | 0.000 | 0.007 | 0.000 | 0.000 | 0.000 | 0.000 |
| 24-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 25-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 26-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 27-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 28-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 29-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 30-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 31-Mar-10 | 0 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| TOTAL | 43 | 0.012 | 0.094 | 0.170 | 0.000 | 0.276 | 0.549 | 0.468 | 0.186 | 0.000 |

| Date | Shedding due to Transmission/Grid Constraints in Central Sector Stations / TTC / ATC VOILATION | TOTAL | TOTAL SHEDDING DUE TO GRID RESTRIC TIONS | Due to T&D Constraints |
| --- | --- | --- | --- | --- |
|  |  |  |  | DTL |
|  | BSES | NDPL | NDMC |  |  | BSES | NDPL | NDMC | MES |
|  | BYPL | BRPL |  |  |  |  | BYPL | BRPL |  |  |  |
| 1 | 12 | 13 | 14 | 15 | 16=8to15 | 17=16+7 | 18 | 19 | 20 | 21 | 22 |
| 01-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 02-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 03-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.047 | 0.000 | 0.069 | 0.002 | 0.000 |
| 04-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.011 | 0.000 | 0.001 | 0.001 | 0.000 |
| 05-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 06-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.010 | 0.000 | 0.000 | 0.000 |
| 07-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.036 | 0.000 | 0.000 | 0.000 | 0.000 |
| 08-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.003 | 0.011 | 0.005 | 0.000 | 0.000 | 0.000 |
| 09-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.001 | 0.000 | 0.005 | 0.000 | 0.000 |
| 10-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 11-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 12-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 13-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.024 | 0.000 | 0.003 | 0.022 | 0.000 | 0.000 |
| 14-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 15-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 16-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.014 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 17-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 1.048 | 1.060 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 18-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.155 | 0.291 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 19-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.063 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 20-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 21-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.003 | 0.021 | 0.021 | 0.000 | 0.000 |
| 22-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.017 | 0.000 | 0.003 | 0.004 | 0.000 | 0.000 |
| 23-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.007 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 24-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 25-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 26-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.067 | 0.000 | 0.000 | 0.000 | 0.000 |
| 27-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.006 | 0.000 | 0.001 | 0.000 | 0.000 |
| 28-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 29-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 30-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 31-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.128 | 0.000 | 0.000 | 0.000 |
| TOTAL | 0.000 | 0.000 | 0.000 | 0.000 | 1.203 | 1.479 | 0.182 | 0.170 | 0.123 | 0.003 | 0.000 |

| DATE | DUE TO T&D CONTRAINTS | OTHER AGENCIES LIKE GENCO, BBMB, BTPS ETC. | THEFT PRONE SHEDDING | TOTAL SHEDDING DUE TO T&D CONSTS. & THEFT PRONE | GRAND TOTAL |
| --- | --- | --- | --- | --- | --- |
|  | DISCOMS |  |  |  |  |
|  | BSES | NDPL |  | BSES | NDPL |  |  |
|  | BYPL | BRPL |  |  | BYPL | BRPL |  |  |  |
| 1 | 23 | 24 | 25 | 2+ | 27 | 28 | 29 | 30=18 to29 | 31=30+17 |
| 01-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.106 | 0.106 | 0.106 |
| 02-Mar-10 | 0.000 | 0.031 | 0.000 | 0.000 | 0.000 | 0.000 | 0.098 | 0.129 | 0.129 |
| 03-Mar-10 | 0.040 | 0.009 | 0.019 | 0.000 | 0.000 | 0.000 | 0.121 | 0.307 | 0.307 |
| 04-Mar-10 | 0.046 | 0.000 | 0.000 | 0.001 | 0.000 | 0.000 | 0.114 | 0.175 | 0.175 |
| 05-Mar-10 | 0.000 | 0.000 | 0.001 | 0.000 | 0.000 | 0.000 | 0.120 | 0.121 | 0.121 |
| 06-Mar-10 | 0.025 | 0.007 | 0.001 | 0.000 | 0.000 | 0.000 | 0.124 | 0.167 | 0.167 |
| 07-Mar-10 | 0.001 | 0.000 | 0.004 | 0.008 | 0.000 | 0.000 | 0.115 | 0.172 | 0.172 |
| 08-Mar-10 | 0.000 | 0.011 | 0.000 | 0.000 | 0.000 | 0.000 | 0.133 | 0.160 | 0.163 |
| 09-Mar-10 | 0.000 | 0.002 | 0.000 | 0.000 | 0.000 | 0.000 | 0.120 | 0.128 | 0.128 |
| 10-Mar-10 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.113 | 0.113 | 0.113 |
| 11-Mar-10 | 0.000 | 0.043 | 0.000 | 0.000 | 0.000 | 0.000 | 0.115 | 0.158 | 0.158 |
| 12-Mar-10 | 0.003 | 0.003 | 0.012 | 0.000 | 0.000 | 0.000 | 0.135 | 0.153 | 0.153 |
| 13-Mar-10 | 0.016 | 0.000 | 0.038 | 0.000 | 0.000 | 0.000 | 0.105 | 0.184 | 0.208 |
| 14-Mar-10 | 0.000 | 0.000 | 0.001 | 0.000 | 0.000 | 0.000 | 0.120 | 0.121 | 0.121 |
| 15-Mar-10 | 0.058 | 0.000 | 0.007 | 0.004 | 0.000 | 0.000 | 0.121 | 0.194 | 0.194 |
| 16-Mar-10 | 0.001 | 0.000 | 0.024 | 0.000 | 0.000 | 0.000 | 0.121 | 0.146 | 0.160 |
| 17-Mar-10 | 0.000 | 0.000 | 0.006 | 0.000 | 0.000 | 0.000 | 0.074 | 0.080 | 1.140 |
| 18-Mar-10 | 0.003 | 0.029 | 0.007 | 0.000 | 0.000 | 0.000 | 0.113 | 0.152 | 0.443 |
| 19-Mar-10 | 0.000 | 0.011 | 0.007 | 0.000 | 0.000 | 0.000 | 0.118 | 0.136 | 0.199 |
| 20-Mar-10 | 0.000 | 0.024 | 0.012 | 0.000 | 0.000 | 0.000 | 0.115 | 0.151 | 0.151 |
| 21-Mar-10 | 0.063 | 0.004 | 0.002 | 0.004 | 0.000 | 0.000 | 0.119 | 0.241 | 0.241 |
| 22-Mar-10 | 0.012 | 0.000 | 0.012 | 0.000 | 0.000 | 0.000 | 0.126 | 0.157 | 0.174 |
| 23-Mar-10 | 0.004 | 0.000 | 0.007 | 0.040 | 0.000 | 0.000 | 0.113 | 0.204 | 0.211 |
| 24-Mar-10 | 0.007 | 0.013 | 0.000 | 0.000 | 0.000 | 0.000 | 0.120 | 0.140 | 0.140 |
| 25-Mar-10 | 0.020 | 0.027 | 0.002 | 0.000 | 0.000 | 0.000 | 0.120 | 0.169 | 0.169 |
| 26-Mar-10 | 0.000 | 0.000 | 0.039 | 0.000 | 0.000 | 0.000 | 0.115 | 0.221 | 0.221 |
| 27-Mar-10 | 0.012 | 0.000 | 0.003 | 0.000 | 0.000 | 0.000 | 0.099 | 0.121 | 0.121 |
| 28-Mar-10 | 0.000 | 0.070 | 0.001 | 0.000 | 0.000 | 0.000 | 0.094 | 0.165 | 0.165 |
| 29-Mar-10 | 0.000 | 0.004 | 0.002 | 0.040 | 0.000 | 0.000 | 0.101 | 0.187 | 0.187 |
| 30-Mar-10 | 0.000 | 0.001 | 0.001 | 0.000 | 0.000 | 0.000 | 0.116 | 0.118 | 0.118 |
| 31-Mar-10 | 0.000 | 0.017 | 0.030 | 0.000 | 0.000 | 0.000 | 0.113 | 0.288 | 0.288 |
| Total | 0.311 | 0.306 | 0.238 | 0.097 | 0.000 | 0.000 | 3.537 | 5.064 | 6.543 |

| DATE | (NET CONS.) | MAXI. DEMAND MET DURING THE DAY | TIME OF OCCUR-RENCE OF MAX DEMAND | SHEDDING AT THIS TIME | UN-REST- RICTED DEMAND | MAXIMUM UN-REST-RICTED DEMAND DURING THE DAY | TIME OF MAX. UN-REST. DEMAND | DEMAND AT THAT TIME | SHEDDING AT THAT TIME |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | In Mus. | IN MW | IN HRS. | IN MW | IN MW | IN MW | HRS. | IN MW | IN MW |
| 1 | 32 | 33 | 34 | 35 | 36=33+35 | 37=39+40 | 38 | 39 | 40 |
| 01-Mar-10 | 39.551 | 2089 | 19:33:47 | 17 | 2106 | 2106 | 19:33:47 | 2089 | 17 |
| 02-Mar-10 | 45.926 | 2529 | 19:16:43 | 0 | 2529 | 2529 | 19:16:43 | 2529 | 0 |
| 03-Mar-10 | 49.936 | 2780 | 19:19:37 | 9 | 2789 | 2789 | 19:19:37 | 2780 | 9 |
| 04-Mar-10 | 51.998 | 2988 | 19:19:05 | 0 | 2988 | 2988 | 19:19:05 | 2988 | 0 |
| 05-Mar-10 | 52.600 | 2871 | 19:18:04 | 0 | 2871 | 2871 | 19:18:04 | 2871 | 0 |
| 06-Mar-10 | 50.803 | 2770 | 19:09:05 | 0 | 2770 | 2770 | 19:09:05 | 2770 | 0 |
| 07-Mar-10 | 47.789 | 2533 | 19:30 | 0 | 2533 | 2533 | 19:30 | 2533 | 0 |
| 08-Mar-10 | 50.383 | 2772 | 19:08:58 | 0 | 2772 | 2772 | 19:08:58 | 2772 | 0 |
| 09-Mar-10 | 51.729 | 2802 | 19:17:22 | 0 | 2802 | 2802 | 19:17:22 | 2802 | 0 |
| 10-Mar-10 | 51.507 | 2802 | 19:25:11 | 0 | 2802 | 2802 | 19:25:11 | 2802 | 0 |
| 11-Mar-10 | 52.264 | 2884 | 19:17:38 | 0 | 2884 | 2884 | 19:17:38 | 2884 | 0 |
| 12-Mar-10 | 53.226 | 2935 | 19:27:46 | 3 | 2938 | 2938 | 19:27:46 | 2935 | 3 |
| 13-Mar-10 | 52.091 | 2842 | 19:17:16 | 0 | 2842 | 2842 | 19:17:16 | 2842 | 0 |
| 14-Mar-10 | 50.243 | 2672 | 19:19:57 | 0 | 2672 | 2672 | 19:19:57 | 2672 | 0 |
| 15-Mar-10 | 52.713 | 2922 | 19:20:17 | 0 | 2922 | 2922 | 19:20:17 | 2922 | 0 |
| 16-Mar-10 | 55.406 | 2989 | 19:19:54 | 6 | 2995 | 2995 | 19:19:54 | 2989 | 6 |
| 17-Mar-10 | 55.715 | 2824 | 19:21:24 | 197 | 3021 | 3021 | 19:21:24 | 2824 | 197 |
| 18-Mar-10 | 55.764 | 3133 | 19:05:05 | 0 | 3133 | 3133 | 19:05:05 | 3133 | 0 |
| 19-Mar-10 | 59.397 | 3177 | 19:21:34 | 0 | 3177 | 3177 | 19:21:34 | 3177 | 0 |
| 20-Mar-10 | 58.368 | 3117 | 19:17:10 | 7 | 3124 | 3124 | 19:17:10 | 3117 | 7 |
| 21-Mar-10 | 54.932 | 2935 | 19:50:25 | 0 | 2935 | 2935 | 19:50:25 | 2935 | 0 |
| 22-Mar-10 | 60.131 | 3301 | 19:19:03 | 0 | 3301 | 3301 | 19:19:03 | 3301 | 0 |
| 23-Mar-10 | 66.531 | 3272 | 19:18:59 | 0 | 3272 | 3272 | 19:18:59 | 3272 | 0 |
| 24-Mar-10 | 61.933 | 3264 | 19:17:24 | 0 | 3264 | 3264 | 19:17:24 | 3264 | 0 |
| 25-Mar-10 | 65.989 | 3364 | 19:02:12 | 2 | 3366 | 3366 | 19:02:12 | 3364 | 2 |
| 26-Mar-10 | 66.617 | 3411 | 19:20:11 | 0 | 3411 | 3411 | 19:20:11 | 3411 | 0 |
| 27-Mar-10 | 64.871 | 3255 | 19:20:56 | 0 | 3255 | 3255 | 19:20:56 | 3255 | 0 |
| 28-Mar-10 | 60.851 | 3012 | 19:35:39 | 0 | 3012 | 3012 | 19:35:39 | 3012 | 0 |
| 29-Mar-10 | 64.649 | 3312 | 19:52:07 | 0 | 3312 | 3312 | 19:52:07 | 3312 | 0 |
| 30-Mar-10 | 68.237 | 3407 | 19:43:22 | 0 | 3407 | 3407 | 19:43:22 | 3407 | 0 |
| 31-Mar-10 | 68.935 | 3406 | 19:18:14 | 0 | 3406 | 3406 | 19:18:14 | 3406 | 0 |
| Total | 1741.085 | 3411 Max |  |  | 3411 Max. | 3411 Max. |  |  |  |

10	LOAD PATTERN OF DELHI ON THE DAY OF PEAK DEMAND MET DURING MARCH 2010 ON 26.03.2010 – 3411 MW at 19:20:11HRS.

All figures in MW

| Hrs. | Demand | Load Shedding | Un-Restricted Demand |
| --- | --- | --- | --- |
| 1.00 | 2461 | 0 | 2461 |
| 2.00 | 2335 | 0 | 2335 |
| 3.00 | 2254 | 0 | 2254 |
| 4.00 | 2208 | 0 | 2208 |
| 5.00 | 2232 | 0 | 2232 |
| 6.00 | 2363 | 0 | 2363 |
| 7.00 | 2511 | 9 | 2520 |
| 8.00 | 2527 | 14 | 2541 |
| 9.00 | 2651 | 0 | 2651 |
| 10.00 | 2995 | 0 | 2995 |
| 11.00 | 3128 | 0 | 3128 |
| 12.00 | 3067 | 13 | 3080 |
| 13.00 | 2990 | 0 | 2990 |
| 14.00 | 3077 | 30 | 3107 |
| 15.00 | 3084 | 5 | 3089 |
| 16.00 | 3132 | 5 | 3137 |
| 17.00 | 3115 | 10 | 3125 |
| 18.00 | 2965 | 51 | 3016 |
| 19.00 | 3349 | 0 | 3349 |
| 19.20.11 | 3411 | 0 | 3411 |
| 20.00 | 3321 | 0 | 3321 |
| 21.00 | 3128 | 3 | 3131 |
| 22.00 | 2983 | 0 | 2983 |
| 23.00 | 2936 | 0 | 2936 |
| 24.00 | 2740 | 0 | 2740 |
| ENERGY IN Mus | 66.617 | 0.221 | 66.838 |

11	LOAD PATTERN OF DELHI ON THE DAY OF MAXIMUM UN-RESTRICTED DEMAND DURING MARCH 2010 – 26.03.2010 – 3411MW at 19:20:11hrs.

All figures in MW

| Hrs. | Demand | Load Shedding | Un-Restricted Demand |
| --- | --- | --- | --- |
| 1.00 | 2461 | 0 | 2461 |
| 2.00 | 2335 | 0 | 2335 |
| 3.00 | 2254 | 0 | 2254 |
| 4.00 | 2208 | 0 | 2208 |
| 5.00 | 2232 | 0 | 2232 |
| 6.00 | 2363 | 0 | 2363 |
| 7.00 | 2511 | 9 | 2520 |
| 8.00 | 2527 | 14 | 2541 |
| 9.00 | 2651 | 0 | 2651 |
| 10.00 | 2995 | 0 | 2995 |
| 11.00 | 3128 | 0 | 3128 |
| 12.00 | 3067 | 13 | 3080 |
| 13.00 | 2990 | 0 | 2990 |
| 14.00 | 3077 | 30 | 3107 |
| 15.00 | 3084 | 5 | 3089 |
| 16.00 | 3132 | 5 | 3137 |
| 17.00 | 3115 | 10 | 3125 |
| 18.00 | 2965 | 51 | 3016 |
| 19.00 | 3349 | 0 | 3349 |
| 19.20.11 | 3411 | 0 | 3411 |
| 20.00 | 3321 | 0 | 3321 |
| 21.00 | 3128 | 3 | 3131 |
| 22.00 | 2983 | 0 | 2983 |
| 23.00 | 2936 | 0 | 2936 |
| 24.00 | 2740 | 0 | 2740 |
| ENERGY IN Mus | 66.617 | 0.221 | 66.838 |

12	LOAD PATTERN OF DELHI ON THE DAY OF MAXIMUM ENERGY CONSUMED

DURING MARCH 2010 – 31.03.2010 – 68.935 Mus

All figures in MW

| Hrs. | Demand | Load Shedding | Un-Restricted Demand |
| --- | --- | --- | --- |
| 1 | 2706 | 0 | 2706 |
| 2 | 2598 | 0 | 2598 |
| 3 | 2473 | 0 | 2473 |
| 4 | 2393 | 0 | 2393 |
| 5 | 2377 | 0 | 2377 |
| 6 | 2443 | 30 | 2473 |
| 7 | 2547 | 33 | 2580 |
| 8 | 2561 | 78 | 2639 |
| 9 | 2706 | 54 | 2760 |
| 10 | 3019 | 0 | 3019 |
| 11 | 3200 | 2 | 3202 |
| 12 | 3251 | 2 | 3253 |
| 13 | 3169 | 2 | 3171 |
| 14 | 3139 | 2 | 3141 |
| 15 | 3169 | 2 | 3171 |
| 16 | 3218 | 2 | 3220 |
| 17 | 3178 | 24 | 3202 |
| 18 | 3066 | 29 | 3095 |
| 19 | 3290 | 0 | 3290 |
| 19.18.14 | 3406 | 0 | 3406 |
| 20 | 3320 | 0 | 3320 |
| 21 | 3183 | 3 | 3186 |
| 22 | 3146 | 0 | 3146 |
| 23 | 3091 | 0 | 3091 |
| 24 | 2879 | 0 | 2879 |
| ENERGY IN Mus | 68.935 | 0.288 | 69.223 |

13	LOAD PATTERN OF DELHI ON THE DAY OF MAXIMUM UNRESTRICTED ENERGY DEMAND DURING MARCH 2010 – 31.03.2010 – 69.223Mus

All figures in MW

| Hrs. | Demand | Load Shedding | Un-Restricted Demand |
| --- | --- | --- | --- |
| 1 | 2706 | 0 | 2706 |
| 2 | 2598 | 0 | 2598 |
| 3 | 2473 | 0 | 2473 |
| 4 | 2393 | 0 | 2393 |
| 5 | 2377 | 0 | 2377 |
| 6 | 2443 | 30 | 2473 |
| 7 | 2547 | 33 | 2580 |
| 8 | 2561 | 78 | 2639 |
| 9 | 2706 | 54 | 2760 |
| 10 | 3019 | 0 | 3019 |
| 11 | 3200 | 2 | 3202 |
| 12 | 3251 | 2 | 3253 |
| 13 | 3169 | 2 | 3171 |
| 14 | 3139 | 2 | 3141 |
| 15 | 3169 | 2 | 3171 |
| 16 | 3218 | 2 | 3220 |
| 17 | 3178 | 24 | 3202 |
| 18 | 3066 | 29 | 3095 |
| 19 | 3290 | 0 | 3290 |
| 19.18.14 | 3406 | 0 | 3406 |
| 20 | 3320 | 0 | 3320 |
| 21 | 3183 | 3 | 3186 |
| 22 | 3146 | 0 | 3146 |
| 23 | 3091 | 0 | 3091 |
| 24 | 2879 | 0 | 2879 |
| ENERGY IN Mus | 68.935 | 0.288 | 69.223 |

14	LOAD DURATION CURVE FOR MARCH 2010

| Load in MW | Percentage of Time |
| --- | --- |
| Above 1400 | 100.00 % |
| Above 1600 | 89.02 % |
| Above 1800 | 83.14 % |
| Above 2000 | 78.15 % |
| Above 2200 | 71.29 % |
| Above 2400 | 55.99 % |
| Above 2600 | 35.50 % |
| Above 2800 | 19.14 % |
| Above 3000 | 7.17 % |
| Above 3200 | 1.82 % |
| Above 3400 | 0.02 % |

15	FREQUENCY ANALYSIS FOR THE MONTH OF MARCH 2010

| Frequency Range in Hz. | Percentage of time |
| --- | --- |
| Above 48.00 | 100 % |
| Above 48.25 | 100 % |
| Above 48.50 | 100 % |
| Above 48.75 | 100 % |
| Above 49.00 | 97.74 % |
| Above 49.25 | 85.23 % |
| Above 49.50 | 55.15 % |
| Above 49.75 | 22.39 % |
| Above 50.00 | 3.35 % |
| Above 50.25 | 0.44 % |
| Above 50.50 | 0.02 % |
| Above 50.75 | 0 % |

16	Voltage Profile of 220 KV sub-sTATIONS in Delhi during MARCH 2010

All figures in kV

| Date | NARELA | GAZIPUR |
| --- | --- | --- |
|  | Max | Min | Max | Min |
| 01-Mar-10 | -- | -- | -- | -- |
| 02-Mar-10 | -- | -- | -- | -- |
| 03-Mar-10 | -- | -- | -- | -- |
| 04-Mar-10 | -- | -- | -- | -- |
| 05-Mar-10 | -- | -- | -- | -- |
| 06-Mar-10 | -- | -- | -- | -- |
| 07-Mar-10 | -- | -- | -- | -- |
| 08-Mar-10 | 223.38 | 210.22 | 233.05 | 213.44 |
| 09-Mar-10 | -- | -- | -- | -- |
| 10-Mar-10 | 220.15 | 206.74 | 226.60 | 212.41 |
| 11-Mar-10 | 221.70 | 206.61 | 230.47 | 207.25 |
| 12-Mar-10 | 222.47 | 204.16 | 232.02 | 212.67 |
| 13-Mar-10 | 220.80 | 206.87 | 230.73 | 216.41 |
| 14-Mar-10 | 222.21 | 205.71 | 234.08 | 215.38 |
| 15-Mar-10 | 221.44 | 207.00 | 231.11 | 212.67 |
| 16-Mar-10 | 220.92 | 207.51 | 229.31 | 213.19 |
| 17-Mar-10 | 222.34 | 203.51 | 232.15 | 213.32 |
| 18-Mar-10 | 222.90 | 206.87 | 231.37 | 217.18 |
| 19-Mar-10 | 220.80 | 201.19 | 231.24 | 202.74 |
| 20-Mar-10 | -- | -- | -- | -- |
| 21-Mar-10 | 223.38 | 208.80 | 232.15 | 218.47 |
| 22-Mar-10 | 222.47 | 204.03 | 232.40 | 214.09 |
| 23-Mar-10 | 220.41 | 207.90 | 232.02 | 217.18 |
| 24-Mar-10 | 224.02 | 206.87 | 231.11 | 215.25 |
| 25-Mar-10 | -- | -- | -- | -- |
| 26-Mar-10 | 221.57 | 205.71 | 230.73 | 213.83 |
| 27-Mar-10 | 221.44 | 208.54 | 231.11 | 216.41 |
| 28-Mar-10 | -- | -- | -- | -- |
| 29-Mar-10 | -- | -- | -- | -- |
| 30-Mar-10 | -- | -- | -- | -- |
| 31-Mar-10 | 221.05 | 208.29 | 230.73 | 206.22 |

17	Voltage Profile of 400 KV sub-sTATIONS in Delhi during MARCH  2010

All figures in kV

| Date | 400kV Bamnauli Grid Sub-Station |
| --- | --- |
|  | Max KV | Max Time | Min KV | Min Time | Average KV |
| 01-Mar-10 | -- | -- | -- | -- | -- |
| 02-Mar-10 | -- | -- | -- | -- | -- |
| 03-Mar-10 | -- | -- | -- | -- | -- |
| 04-Mar-10 | -- | -- | -- | -- | -- |
| 05-Mar-10 | -- | -- | -- | -- | -- |
| 06-Mar-10 | -- | -- | -- | -- | -- |
| 07-Mar-10 | -- | -- | -- | -- | -- |
| 08-Mar-10 | 411.30 | 21.14.34 | 386.20 | 18.41.26 | 398.16 |
| 09-Mar-10 | -- | -- | -- | -- | -- |
| 10-Mar-10 | 405.20 | 01.07.01 | 381.98 | 10.15.52 | 395.03 |
| 11-Mar-10 | 409.18 | 05.02.31 | 382.92 | 12.18.55 | 395.23 |
| 12-Mar-10 | 407.78 | 05.05.38 | 376.12 | 10.10.15 | 396.00 |
| 13-Mar-10 | 407.54 | 18.01.12 | 385.74 | 09.49.07 | 396.49 |
| 14-Mar-10 | 411.30 | 17.11.20 | 379.64 | 12.09.03 | 398.43 |
| 15-Mar-10 | 406.61 | 05.03.39 | 384.33 | 11.32.02 | 396.55 |
| 16-Mar-10 | 407.31 | 05.06.31 | 383.39 | 10.20.41 | 396.30 |
| 17-Mar-10 | 408.95 | 02.01.38 | 378.70 | 11.08.23 | 397.16 |
| 18-Mar-10 | 410.36 | 03.16.22 | 385.27 | 10.11.27 | 398.36 |
| 19-Mar-10 | 408.95 | 01.05.35 | 376.36 | 11.35.59 | 395.02 |
| 20-Mar-10 | -- | -- | -- | -- | -- |
| 21-Mar-10 | 409.89 | 03.36.58 | 387.38 | 11.21.58 | 400.40 |
| 22-Mar-10 | 410.83 | 18.02.59 | 379.64 | 10.07.55 | 396.86 |
| 23-Mar-10 | 408.72 | 03.04.22 | 384.33 | 10.28.20 | 397.72 |
| 24-Mar-10 | 408.48 | 05.04.47 | 382.22 | 11.10.09 | 395.85 |
| 25-Mar-10 | -- | -- | -- | -- | -- |
| 26-Mar-10 | 408.48 | -- | 379.40 | -- | 395.72 |
| 27-Mar-10 | 408.72 | 03.59.16 | 385.03 | 11.27.09 | 397.80 |
| 28-Mar-10 | -- | -- | -- | -- | -- |
| 29-Mar-10 | -- | -- | -- | -- | -- |
| 30-Mar-10 | -- | -- | -- | -- | -- |
| 31-Mar-10 | 407.31 | 08.27.18 | 385.03 | 14.51.27 | 395.51 |

| Date | 400kV Bawana Grid Sub-Station |
| --- | --- |
|  | Max KV | Max Time | Min KV | Min Time | Average KV |
| 01-Mar-10 | -- | -- | -- | -- | -- |
| 02-Mar-10 | -- | -- | -- | -- | -- |
| 03-Mar-10 | -- | -- | -- | -- | -- |
| 04-Mar-10 | -- | -- | -- | -- | -- |
| 05-Mar-10 | -- | -- | -- | -- | -- |
| 06-Mar-10 | -- | -- | -- | -- | -- |
| 07-Mar-10 | -- | -- | -- | -- | -- |
| 08-Mar-10 | 415.05 | 21.13.44 | 391.36 | 18.42.46 | 402.66 |
| 09-Mar-10 | -- | -- | -- | -- | -- |
| 10-Mar-10 | 408.95 | 01.06.21 | 388.08 | 07.17.41 | 399.83 |
| 11-Mar-10 | 412.47 | 05.02.41 | 386.91 | 12.18.35 | 399.35 |
| 12-Mar-10 | 411.30 | 05.05.18 | 381.05 | 10.10.15 | 400.04 |
| 13-Mar-10 | 411.06 | 18.01.22 | 389.72 | 09.52.57 | 399.94 |
| 14-Mar-10 | 414.58 | 17.10.50 | 383.16 | 12.08.53 | 401.67 |
| 15-Mar-10 | 409.89 | 05.03.49 | 389.96 | 10.43.20 | 400.85 |
| 16-Mar-10 | 411.06 | 05.06.51 | 387.85 | 10.19.21 | 400.08 |
| 17-Mar-10 | 412.23 | 02.01.48 | 383.16 | 11.08.03 | 401.25 |
| 18-Mar-10 | 413.87 | 03.19.22 | 389.25 | 12.17.24 | 402.54 |
| 19-Mar-10 | 412.23 | 01.05.25 | 381.51 | 11.35.49 | 399.25 |
| 20-Mar-10 | -- | -- | -- | -- | -- |
| 21-Mar-10 | 413.41 | 16.02.44 | 390.89 | 11.23.08 | 404.30 |
| 22-Mar-10 | 414.58 | 18.02.59 | 384.09 | 10.07.55 | 400.99 |
| 23-Mar-10 | 411.30 | 23.56.05 | 389.96 | 12.45.49 | 401.30 |
| 24-Mar-10 | 412.23 | 00.00.06 | 386.44 | 11.10.19 | 400.60 |
| 25-Mar-10 | -- | -- | -- | -- | -- |
| 26-Mar-10 | 411.53 | -- | 384.09 | -- | 399.55 |
| 27-Mar-10 | 412.23 | 03.59.26 | 388.55 | 11.26.49 | 401.19 |
| 28-Mar-10 | -- | -- | -- | -- | -- |
| 29-Mar-10 | -- | -- | -- | -- | -- |
| 30-Mar-10 | -- | -- | -- | -- | -- |
| 31-Mar-10 | 410.83 | 08.27.28 | 386.20 | 14.54.27 | 399.14 |

18	Details of Lumped Capacitors at nearest 220 kV substation

a)	Delhi Transco Limited (DTL)

| Name of the Sub-stn | Voltage (KV) | Installed Capacity (MVAR) | Working Capacity (MVAR) | Remarks |
| --- | --- | --- | --- | --- |
| Patparganj | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 5.04 | 5.04 |  |
| Kashmere Gate | 11 | 5.04 | 5.04 |  |
| Gazipur | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Okhla | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 5.04 | 5.04 |  |
| Lodhi Road | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 5.976 | 0 | TEMPORARILY DISMANTLED ON 11.11.2006 FOR TAKING OUT 100MVA PR. TX.-I |
| Sarita Vihar | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Vasant Kunj | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Mehrauli | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Najafgarh | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Narela | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |

| Name of the sub-stn | Voltage (KV) | Installed Capacity (MVAR) | Working Capacity (MVAR) | Remarks |
| --- | --- | --- | --- | --- |
| Shalimar Bagh | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 6 | 6 |  |
| Rohini | 66 | 20 | 20 |  |
|  | 66 | 20 | 20 |  |
|  | 11 | 6 | 6 |  |
| Gopalpur | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 5.04 | 5.04 |  |
| Subzi Mandi | 11 | 6 | 6 |  |
| Kanjhawala | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Park Street | 66 | 20 | 20 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
| Papankalan-I | 66 | 20 | 20 |  |
|  | 11 | 5.04 | 5.04 |  |
| Naraina | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 11 | 5.04 | 5.04 |  |
|  | Total Capacity | 749.496 | 743.700 |  |

B.        IPGCL

| Name of the Sub-stn | Voltage (KV) | Installed Capacity (MVAR) | Working Capacity (MVAR) | Remarks |
| --- | --- | --- | --- | --- |
| IP | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 0 | OUT SINCE 08.04.2005. CELLS DAMAGED, ORDER PLACED ON BHEL |
| RPH | 11 | 5.04 | 5.04 |  |
|  | 33 | 10 | 10 |  |
|  | 33 | 10 | 10 |  |
|  | Total Capacity | 65.04 | 55.04 |  |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY IN MVAR |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 1 | IP STATION |  | 30 |  | 30 |
| 1 | Kamla Market |  |  | 9.65 | 9.65 |
| 2 | Minto Road |  |  | 5.45 | 5.45 |
| 3 | GB Pant Hosp |  |  | 5.45 | 5.45 |
| 4 | Delhi Gate |  |  | 10.9 | 10.9 |
| 5 | Tilakmarg |  |  | 5.04 | 5.04 |
| 6 | Electric Lane |  |  | 5.04 | 5.04 |
| 7 | Connaught Place |  |  | 10.08 | 10.08 |
| 8 | Kilokri |  | 10 | 10.48 | 20.48 |
| 9 | NDSE |  |  | 5.04 | 5.04 |
| 10 | AIIMS |  | 10 | 5.04 | 15.04 |
| 11 | Nizamuddin |  |  | 5.04 | 5.04 |
| 12 | Exhibition-I |  | 10 |  | 10 |
| 13 | Exhibition-II |  |  |  |  |
| 14 | Defence Colony |  |  | 10.9 | 10.9 |
| 15 | IG Stadium |  | 10 |  | 10 |
| 16 | Lajpat Nagar |  |  | 5.04 | 5.04 |
|  | Total |  |  |  | 163.15 |
| 2 | IP Extn. |  |  |  |  |
| 1 | School Lane |  |  | 5.04 | 5.04 |
| 2 | Scindia House |  |  | 5.04 | 5.04 |
| 3 | Vidyut Bhawan |  |  | 15.12 | 15.12 |
| 4 | Nirman Bhawan |  |  | 5.04 | 5.04 |
| 5 | Dalhousie Road |  |  | 5.04 | 5.04 |
|  | Total |  |  |  | 35.28 |
| 3 | RPH Station |  | 20 | 5.04 | 25.04 |
| 1 | Lahori Gate |  |  | 10.45 | 10.45 |
| 2 | Jama Masjid |  |  | 5.03 | 5.03 |
| 4 | Kamla Market |  |  | 5.45 | 5.45 |
| 5 | Minto Road |  |  | 5.45 | 5.45 |
| 6 | GB Pant Hosp |  |  | 5.03 | 5.03 |
| 7 | IG Stadium |  |  | 5.45 | 5.45 |
| 8 | IP Estate |  |  | 10.9 | 10.9 |
|  | Total |  |  |  | 72.8 |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY IN MVAR |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 4 | Parkstreet S/stn | 20 | 20 |  | 40 |
| 1 | Shastri Park |  | 10 | 5.45 | 15.45 |
| 2 | Faiz Road |  |  | 10.9 | 10.9 |
| 3 | Motia Khan |  |  | 16.3 | 16.3 |
| 4 | Parshad Nagar |  |  | 16.3 | 16.3 |
| 5 | Anand Parbat |  |  | 10.8 | 10.8 |
| 6 | Shankar Road |  |  | 5.04 | 5.04 |
| 7 | Rama Road |  |  | 14.4 | 14.4 |
| 8 | Baird Road |  |  | 10.08 | 10.08 |
| 9 | Hanuman Road |  |  | 5.04 | 5.04 |
| 10 | Pusa |  |  | 7.2 | 7.2 |
| 11 | Ridge Valley |  |  |  |  |
| 12 | SJ Airport |  |  | 5.04 | 5.04 |
| 13 | B. D. Marg |  |  |  |  |
|  | Total |  |  |  | 156.55 |
| 5 | Naraina S/stn |  | 20 | 5.04 | 25.04 |
| 1 | DMS |  |  | 10.45 | 10.45 |
| 2 | Mayapuri |  | 10 | 5 | 15 |
| 3 | Inderpuri |  | 10 | 5.04 | 15.04 |
| 4 | Rewari line |  |  | 7.2 | 7.2 |
| 5 | Khyber Lane |  | 10 |  | 10 |
| 6 | Kirbi Place |  |  | 5 | 5 |
| 7 | Payal Cinema |  |  | 14.4 | 14.4 |
|  | Total |  |  |  | 102.13 |
| 6 | Mehrauli S/stn | 80 |  | 5.04 | 85.04 |
| 1 | Adchini |  |  | 15.12 | 15.12 |
| 2 | Andheria Bagh |  |  | 10.85 | 10.85 |
| 3 | IIT |  |  | 10.9 | 10.9 |
| 4 | JNU |  | 10 | 10.08 | 20.08 |
| 5 | Bijwasan |  |  | 10.08 | 10.08 |
| 6 | DC Saket |  | 10 | 4.54 | 14.54 |
| 7 | Malviya Nagar | 20 |  |  | 20 |
| 8 | C Dot |  |  |  |  |
| 9 | Vasant kunj B-Blk | 20 |  | 10.9 | 30.9 |
| 10 | Vasant kunj C-Blk | 20 |  | 5.45 | 25.45 |
| 11 | Palam |  |  |  |  |
| 12 | IGNOU |  |  |  |  |
| 13 | R. K. Puram-I |  |  | 10.08 | 10.08 |
| 14 | Vasant Vihar |  |  | 10.08 | 10.08 |
| 15 | Bhikaji Cama Place |  | 10 | 10.08 | 20.08 |
|  | Total |  |  |  | 283.2 |
| 7 | Vasantkunj S/stn | 40 |  | 5.04 | 45.04 |
| 2 | R. K. Puram-II |  |  | 3.6 | 3.6 |
| 4 | Vasant kunj C-Blk |  |  | 5.04 | 5.04 |
| 5 | Vasant kunj D-Blk | 20 |  | 10.25 | 30.25 |
| 8 | Race Course |  |  | 5.04 | 5.04 |
| 9 | Bapu Dhaam |  |  | 5.04 | 5.04 |
| 10 | Nehru Park |  |  | 5.04 | 5.04 |
| 12 | Ridge Valley |  |  |  |  |
|  | Total |  |  |  | 99.05 |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY IN MVAR |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 8 | Okhla S/stn | 60 | 10 | 5.04 | 75.04 |
| 1 | Balaji |  |  | 7.2 | 7.2 |
| 2 | East of Kailash |  |  | 10 | 10 |
| 3 | Alaknanda |  |  | 10.85 | 10.85 |
| 4 | Malviya Nagar |  | 20 | 10.49 | 30.49 |
| 5 | Masjid Moth |  |  | 15.94 | 15.94 |
| 6 | Nehru Place |  |  | 21.35 | 21.35 |
| 7 | Okhla Ph-I | 20 |  | 10.9 | 30.9 |
| 8 | Okhla Ph-II |  | 20.93 | 10.49 | 31.42 |
| 9 | Shivalik |  |  | 10.9 | 10.9 |
| 10 | Batra |  |  | 15.8 | 15.8 |
| 11 | VSNL |  |  | 10.8 | 10.8 |
| 12 | Siri Fort |  |  | 10.49 | 10.49 |
| 13 | Tuglakabad |  |  | 10.8 | 10.8 |
|  | Total |  |  |  | 291.98 |
| 9 | Lodhi Road S/stn |  | 20 |  | 20 |
| 1 | Defence Colony |  |  |  |  |
| 2 | Hudco |  |  | 10.9 | 10.9 |
| 4 | Lajpat Nagar |  |  | 5.04 | 5.04 |
| 5 | Nizamuddin |  |  | 5.45 | 5.45 |
| 6 | Vidyut Bhawan |  |  | 10.08 | 10.08 |
| 7 | Kidwai Nagar |  |  | 5.04 | 5.04 |
| 8 | Ex. Gr. II |  |  |  |  |
| 9 | IHC |  |  |  |  |
|  | Total |  |  |  | 56.51 |
| 10 | Sarita Vihar S/stn | 20 |  | 5.04 | 25.04 |
| 1 | Sarita Vihar |  |  | 10.08 | 10.08 |
| 2 | MCIE |  |  | 10.06 | 10.06 |
| 3 | Mathura Road | 20 |  | 5.04 | 25.04 |
| 4 | Jamia Millia |  |  | 5.4 | 5.4 |
| 5 | Sarai Julena |  | 10 | 10.9 | 20.9 |
|  | Total |  |  |  | 96.52 |
| 11 | Wazirabad |  |  |  |  |
| 1 | Bhagirathi |  | 10 | 10.9 | 20.9 |
| 2 | Ghonda | 20 | 20 | 15.94 | 55.94 |
| 3 | Seelam Pur |  | 10 | 21.39 | 31.39 |
| 4 | Dwarkapuri |  |  | 10.06 | 10.06 |
| 5 | Nandnagri | 20 |  | 16.35 | 36.35 |
| 6 | Yamuna Vihar |  |  | 10.8 | 10.8 |
| 7 | East of Loni Road |  |  | 10.8 | 10.8 |
| 8 | Shastri Park |  |  | 10.9 | 10.9 |
| 9 | Karawal Nagar |  |  | 5.4 | 5.4 |
|  | Total |  |  |  | 192.54 |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY MVAR |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 12 | Geeta Colony |  |  |  |  |
| 1 | Geeta Colony |  |  | 10.49 | 10.49 |
| 2 | Kanti Nagar |  |  | 10.9 | 10.9 |
| 3 | Kailash Nagar |  |  | 15.48 | 15.48 |
| 4 | Seelam Pur |  |  |  |  |
| 5 | Shakar Pur |  |  |  |  |
|  | Total |  |  |  | 36.87 |
| 13 | Gazipur S/stn | 40 |  | 5.04 | 45.04 |
| 1 | Dallupura | 20 |  | 10.9 | 30.9 |
| 2 | Vivek Vihar |  |  | 9.57 | 9.57 |
| 3 | GT Road |  |  | 10.85 | 10.85 |
| 4 | Kondli | 20 |  | 10.45 | 30.45 |
| 5 | MVR-I |  |  | 10.9 | 10.9 |
| 6 | MVR-II | 20 |  | 10.9 | 30.9 |
| 7 | PPG Ind. Area |  |  | 10.06 | 10.06 |
|  | Total |  |  |  | 178.67 |
| 14 | Patparganj S/stn | 40 | 20 | 5.04 | 65.04 |
| 1 | GH-I | 20 |  | 10.45 | 30.45 |
| 2 | GH-II | 20 |  | 10.9 | 30.9 |
| 3 | CBD |  | 10 | 14.94 | 24.94 |
| 4 | Guru Angad Nagar |  |  | 15.49 | 15.49 |
| 5 | Karkadooma |  | 10 | 10.44 | 20.44 |
| 6 | Preet Vihar |  |  | 10.07 | 10.07 |
| 7 | CBD-II |  |  | 7.2 | 7.2 |
| 8 | Shakarpur |  |  | 5.4 | 5.4 |
| 9 | Jhilmil |  |  | 9 | 9 |
| 10 | Dilshad Garden | 20 |  | 16.35 | 36.35 |
| 11 | Khichripur | 20 |  | 10.49 | 30.49 |
| 12 | Mother Dairy |  |  |  |  |
| 13 | Scope Building |  |  |  |  |
| 14 | Vivek Vihar |  |  |  |  |
|  | Total |  |  |  | 285.77 |
| 15 | Najafgarh S/stn | 60 |  | 5.04 | 65.04 |
| 1 | A4 Paschim Vihar |  |  | 10.9 | 10.9 |
| 2 | Nangloi | 20 |  | 15.85 | 35.85 |
| 3 | Nangloi W/W | 20 |  | 5.45 | 25.45 |
| 4 | Pankha Road |  |  | 15.69 | 15.69 |
| 5 | Jaffarpur |  |  | 15.49 | 15.49 |
| 7 | Sagarpur |  |  | 15.9 | 15.9 |
| 8 | Paschimpuri |  | 10 | 15.53 | 25.53 |
| 9 | Paschim Vihar | 40 |  | 15.44 | 55.44 |
| 10 | Mukherjee Park |  |  | 15.49 | 15.49 |
| 11 | Udyog Nagar |  |  | 10.08 | 10.08 |
| 12 | Choukhandi |  |  | 10.08 | 10.08 |
|  | Total |  |  |  | 300.94 |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 16 | Pappankalan-I S/stn | 20 |  | 5.04 | 25.04 |
| 1 | Bindapur | 20 |  | 15.9 | 35.9 |
| 2 | Bodella-I | 20 |  | 15.9 | 35.9 |
| 3 | Bodella-II | 20 |  | 14.53 | 34.53 |
| 4 | DC Febakpuri |  |  | 10.04 | 10.04 |
| 5 | G-2 PPK (Nasirpur) |  |  | 10.9 | 10.9 |
| 6 | G-5 PPK (Matiala) |  |  | 15.53 | 15.53 |
| 7 | G-6 PPK |  |  | 5.45 | 5.45 |
| 8 | Harinagar | 20 |  | 10.49 | 30.49 |
|  | Total |  |  |  | 203.78 |
| 17 | BBMB Rohtak Road |  |  |  |  |
| 1 | S.B. Mill |  |  | 10.08 | 10.08 |
| 1 | GTK Road |  |  | 12.64 | 12.64 |
| 1 | Ram Pura |  |  | 12.25 | 12.25 |
| 1 | Rohtak Road |  |  | 10.08 | 10.08 |
| 1 | Vishal |  | 10 | 5 | 15 |
| 1 | Madipur |  |  | 10.43 | 10.43 |
| 1 | Sudershan Park |  |  | 10.99 | 10.99 |
|  | Total |  |  |  | 81.47 |
| 18 | Shalimarbagh S/stn |  | 40 | 6 | 46 |
| 1 | S.G.T. Nagar |  |  | 13.15 | 13.15 |
| 2 | Wazirpur-1 |  |  | 18.8 | 18.8 |
| 3 | Wazirpur-2 |  |  | 14.4 | 14.4 |
| 4 | Shalimarbagh |  |  | 5.44 | 5.44 |
| 5 | Ashok Vihar |  |  | 20.47 | 20.47 |
| 6 | Rani Bagh |  |  | 14.4 | 14.4 |
| 7 | Haiderpur |  |  | 13.15 | 13.15 |
| 8 | SMB Fsc |  |  | 7.2 | 7.2 |
|  | Total |  |  |  | 153.01 |
| 19 | Subzimandi S/stn |  |  | 6 | 6 |
| 1 | Shakti Nagar |  |  | 5.04 | 5.04 |
| 2 | Gulabibagh |  |  | 7.32 | 7.32 |
| 3 | Shahzadabagh |  |  | 18.19 | 18.19 |
| 4 | Tripolia |  |  | 14.4 | 14.4 |
| 5 | B. G. Road |  |  |  |  |
|  | Total |  |  |  | 50.95 |
| 20 | Narela S/stn | 40 |  | 5.04 | 45.04 |
| 1 | A-7 Narela |  |  | 14.4 | 14.4 |
| 2 | AIR Kham pur |  |  | 13.15 | 13.15 |
| 3 | Badli | 20 |  | 5.95 | 25.95 |
| 4 | DSIDC Narela-1 | 20 |  | 5.95 | 25.95 |
| 5 | DSIDC Narela-2 |  |  | 14.4 | 14.4 |
| 6 | Jahangirpuri |  |  |  |  |
|  | Total |  |  |  | 138.89 |

| Sl. No | Name of the Grid S/Sub-Station | INSTALLED CAPACITY IN MVAR |
| --- | --- | --- |
|  |  | 66KV | 33kV | 11kV | TOTAL |
| 21 | Gopalpur S/stn |  | 30 | 5.04 | 35.04 |
| 1 | Azad Pur |  |  | 21.6 | 21.6 |
| 2 | Hudson Lane |  |  | 5.95 | 5.95 |
| 3 | Wazirabad |  |  | 7.2 | 7.2 |
| 4 | Indra Vihar |  |  | 5.95 | 5.95 |
| 5 | Tri Nagar |  |  | 14.4 | 14.4 |
| 6 | GTK Road |  |  | 12.64 | 12.64 |
| 7 | Jahangirpuri | 20 | 20 | 5.95 | 45.95 |
| 8 | DIFR |  |  | 7.2 | 7.2 |
| 8 | Civil lines |  |  |  |  |
|  | Total |  |  |  | 155.93 |
| 22 | Rohini S/stn | 40 |  | 6 | 46 |
| 1 | Rohini Sec-22 |  |  | 14.4 | 14.4 |
| 2 | Rohini Sec-23 | 20 |  | 5.95 | 25.95 |
| 3 | Rohini Sec-24 |  |  | 7.2 | 7.2 |
| 4 | Rohini-1 |  |  | 5.95 | 5.95 |
| 5 | Rohini-2 |  |  | 13.15 | 13.15 |
| 6 | Rohini-3 |  |  | 5.95 | 5.95 |
| 7 | Rohini-4 |  |  | 11.9 | 11.9 |
| 8 | Rohini-5 |  |  | 13.15 | 13.15 |
| 9 | Rohini-6 | 20 |  | 5.95 | 25.95 |
| 10 | Mangolpuri-1 |  |  | 20.35 | 20.35 |
| 11 | Mangolpuri-2 | 20 |  | 6 | 26 |
| 12 | Saraswati Garden |  |  | 11.9 | 11.9 |
| 13 | Pitam Pura-1 | 20 |  | 12.6 | 32.6 |
| 14 | Pitam Pura-2 |  |  | 12.24 | 12.24 |
| 15 | Pitam Pura-3 |  |  | 7.32 | 7.32 |
|  | Total |  |  |  | 280.01 |
| 23 | Kanjhawala S/stn | 20 |  | 5.04 | 25.04 |
| 1 | Bawana Clear Water |  |  | 14.64 | 14.64 |
| 2 | Pooth Khoord |  |  | 7.2 | 7.2 |
|  | Total |  |  |  | 46.88 |
| 24 | BAWANA S/stn |  |  |  |  |
| 1 | Bawana S/stn No. 6 |  |  | 14.64 | 14.64 |
| 2 | Bawana S/stn No. 7 |  |  | 7.2 | 7.2 |
|  | Total |  |  |  | 21.84 |
| 25 | Kashmeregate |  |  | 5.04 | 5.04 |
| 1 | Civil lines |  |  | 12 | 12 |
| 2 | Town Hall |  |  | 10.49 | 10.49 |
| 3 | Fountain |  |  | 5.45 | 5.45 |
|  | Total |  |  |  | 32.98 |
| 26 | Pappankalan-II |  |  |  |  |
| 1 | DMRC-I |  |  |  |  |
| 2 | DMRC-II |  |  |  |  |
|  | Total |  |  |  | 0 |

20	DETAILS OF BREAK-DOWNS

| SLno | Occurrence of Break-down | details of the Breakdown | TIME OF RESTORATION | Remarks |
| --- | --- | --- | --- | --- |
|  | Date | Time |  | Date | time |  |
| 01 | 01.03.10 | 12.01 | 220KV MANDOLA – GOPALPUR CKT-II | 01.03.10 | 12.14 | CKT. TRIPPED ON DIST. PROT. `B’ PHASE ZONE-I AT MANDOLA AND ON DIST PROT `RYB’ PHASE ZONE-I AT GOPALPUR. |
| 02 | 02.03.10 | 14.58 | 220KV SARITA VIHAR - MAHARANI BAGH CKT | 02.03.10 | 15.08 | CKT. TRIPPED ON DIST PROT `AB’ PHASE ZONE-I AT SARITA VIHAR AND ON DIST PROT ZONE-I AT MAHARANI BAGH. |
| 03 | 02.03.10 | 15.30 | 220KV SARITA VIHAR - MAHARANI BAGH CKT | 02.03.10 | 17.02 | CKT. TRIPPED ON DIST PROT ZONE-I, 186A, 186B AT SARITA VIHAR AND ON DIST PROT ZONE-I AT MAHARANI BAGH. |
| 04 | 02.03.10 | 16.22 | 220KV PRAGATI – SARITA VIHAR CKT. | 02.03.10 | 16.50 | CKT. TRIPPED ON DIST PROT `ABC’ PHASE ZONE-I AT SARITA VIHAR AND ON ACTIVE GROUP-I, DIST PROT ABC’ PHASE ZONE-I, 86, 186 AT PRAGATI |
| 05 | 02.03.10 | 22.17 | 220KV IP – RPH CKT-II | 02.03.10 | 23.32 | CKT. TRIPPED ON 86A, 86B, 86X, 195C, DIST PROT `BC’ PHASE ZONE-II, 195C AT IP. NO TRIPPING AT RPH |
| 06 | 03.03.10 | 16.18 | 220/66KV 100MVA PR. TR.-II AT PARK STREET | 04.03.10 | 03.35 | TR. TRIPPED ON DIFFERENTIAL, 86A, 86 ALONG WITH 66KV I/C-II WHICH TRIPPED WITHOUT INDICATION |
| 07 | 03.03.10 | 22.39 | 66/11KV 20MVA PR. TR.-II AT PAPPANKALAN-II | 04.03.10 | 01.19 | TR. TRIPPED ON LBB PROTECTION, 86, OIL TEMP HIGH ALARM |
| 08 | 03.03.10 | 23.43 | 220/33KV 100MVA PR. TR.-II AT PARK STREET | 03.03.10 | 23.58 | TR. TRIPPED ON 64REF, 86B ALONG WITH 33KV I/C-II WHICH TRIPPED WITHOUT INDICATION. 33KV BUS COUPLER ALSO TRIPPED ON 80C, 27AB. TR. TRIPPED WHILE ARRANGING SHUT-DOWN ON 33KV BUS-I. |
| 09 | 06.03.10 | 13.50 | 220KV BAMNAULI – MEHRAULI CKT-I | 06.03.10 | 13.54 | CKT. TRIPPED ON DIST PROT. `A’ PHASE ZONE-II AT BAMNAULI. NO TRIPPING AT MEHRAULI. |
| 10 | 07.03.10 | 18.30 | 220KV PATPARGANJ – IP CKT-I | 07.03.10 | 18.39 | CKT. TRIPPED ON DIST PROT `RYB’ PHASE ZONE-I AT IP AND ON 186, 186, AT PATPARGANJ due to operation of BUS BAR PROTECTION |
| 11 | 07.03.10 | 18.30 | 220KV PATPARGANJ – GEETA COLONY CKT-I | 07.03.10 | 20.07 | AT PATPARGANJ ckt tripped due to operation of BUS BAR PROTECTION |
| 12 | 07.03.10 | 18.30 | 220/33KV 100MVA PR. TR.-I AND 220/33KV 50MVA PR. TR AT PATPARGANJ | 07.03.10 | 19.15 | tx. tripped due to operation of BUS BAR PROTECTION. 100MVA AND 50MVA PR. TR. ENERGIZED AT 19.12HRS. AND 19.15HRS. RESPECTIVELY |
| 13 | 08.03.10 | 17.58 | 220/66KV 100MVA PR. TR.-I AT PAPPANKALAN-II | 08.03.10 | 18.52 | TR. TRIPPED ON LBB PROTECTION, MASTER TRIP ALONG WITH 66KV I/C-I WHICH TRIPPED ON E/F, LBB PROTECTION, IDMT, E/F. |
| 14 | 08.03.10 | 20.48 | 66/33KV 30MVA PR. TR.-II AT PARK STREET | 08.03.10 | 21.34 | TR. TRIPPED WHILE NORMALIZING 33KV BUS-I. |
| 15 | 08.03.10 | 20.56 | 66/33KV 30MA PR. TR.-II AT PARK STREET | 08.03.10 | 20.56 | TR. TRIPPED ON O/C, E/F, 86. |
| 16 | 09.03.10 | 09.37 | 220KV BAMNAULI – NAJAFGARH CKT-I & II | 09.03.10 | 09.40 | AT NAJAFGARH CKT. TRIPPED ON 186. no tripping at bamnauli |
| 17 | 09.03.10 | 18.30 | 220KV GOPALPUR – SUBZI MANDI CKT-I | 09.03.10 | 18.38 | at gopalpur CKT. TRIPPED WITHOUT INDICATION. no tripping at subzi mandi |
| 18 | 10.03.10 | 12.43 | 220/33KV 100MVA PR. TR.-I AT GEETA COLONY | 10.03.10 | 18.01 | TR. TRIPPED ON BUCHoltZ, 86, 30E ALONG WITH 33KV I/C-I WHICH TRIPPED ON 30. |
| 19 | 10.03.10 | 12.32 | 220KV MANDOLA – WAZIRABAD CKT-IV | 10.03.10 | 17.45 | CKT. TRIPPED On DIST PROT `YB’ PHASE ZONE-I AT MANDOLA AND ON RXME18, DIST PROT `RB’ PHASE ZONE-I AT WAZIRABAD. |
| 20 | 13.03.10 | 10.16 | 220KV SARITA VIHAR – PRAGATI CKT. | 13.03.10 | 10.42 | CKT. TRIPPED ON ACTIVE GROUP-I, DIST PROT `C’ PHASE ZONE-I AT PRAGATI AND ON AUTO RECLOSE LOCK OUT, 186A&B, DIST PROT ABC PHASE ZONE-I AT SARITA VIHAR. |
| 21 | 14.03.10 | 15.37 | 220KV WAZIRABAD – GEETA COLONY CKT-I | 14.03.10 | 23.05 | CKT. TRIPPED ON GENERAL TRIP, DIST PROT `RYB’PHASE AT WAZIRABAD AND ON DIST PROT ABC’ PHASE ZONE-I AT GEETA COLONY. |

| SLno | Occurrence of Break-down | details of the Breakdown | TIME OF RESTORATION | Remarks |
| --- | --- | --- | --- | --- |
|  | Date | Time |  | Date | time |  |
| 22 | 14.03.10 | 17.11 | 220KV WAZIRABAD – KASHMIRI GATE CKT-II | 14.03.10 | 18.18 | CKT. TRIPPED ON GSC’FTWL1, L2, L3 ZONE-I AT WAZIRABAD. NO TRIPPING AT KASHMIRI GATE |
| 23 | 17.03.10 | 18.28 | 33/11KV 20MVA PR. TR.-I AT LODHI ROAD | 18.03.10 | 00.35 | 11KV ½ BUS BAR FLASHED DUE TO FAULT IN 11KV O/G CABINET FEEDER. |
| 24 | 21.03.10 | 12.28 | 33/11KV 16MVA PR.TR.-II AT NARAINA |  |  |  |
| 25 | 21.03.10 | 12.48 | 220KV BTPS – MEHRAULI CKT-I | 21.03.10 | 13.02 | CKT. TRIPPED ON O/C `C’ PHASE AT BTPS. no tripping at mehrauli |
| 26 | 21.03.10 | 14.39 | 220KV PATPARGANJ – GEETA COLONY CKT-II | 21.03.10 | 15.15 | CKT. TRIPPED ON 186, 85/VAA, E/F, ACTIVE GROUP-I, DIST PRROT ABC’ PHASE ZONE-I AT PATPARGANJ AND ON MAIN –I & ii ACTIVE GROUP-I, DIST PROT zone-i, 3-ɸ trip AT GEETA COLONY |
| 27 | 21.03.10 | 14.45 | 220KV GOPALPUR – SUBZI MANDI CKT-I | 21.03.10 | 15.02 | CKT. TRIPPED ON DIST PROT `RYB’ PHASE ZONE-I AT GOPALPUR. NO TRIPPING AT SUBZI MANDI. |
| 28 | 22.03.10 | 21.51 | 220KV MANDOLA – NARELA CKT-II | 24.03.10 | 17.31 | CKT. TRIPPED ON DIST PROT `RYB’ PHASE ZONE-I AT MANDOLA. NO TRIPPING AT NARELA |
| 29 | 23.03.10 | 14.45 | 220KV NARELA – ROHTAK ROAD CKT.-I | 24.03.10 | 17.29 | CKT. TRIPPED ON MAIN-I DIST PROT `ABC’ PHASE ZONE-I MAIN-II DIST PROT ABC’ PHASE ZONE-I, 186 AT NARELA. |
| 30 | 25.03.10 | 12.23 | 220/66kv 100mva pr. tr.-iv at najafgarh | 25.03.10 | 12.37 | tr. tripped on 86, 30a |
| 31 | 26.03.10 | 13.15 | 220kv btps – noida – gazipur ckt. | 26.03.10 | 13.17 | ckt. tripped on auxiliary relay, 186a&b at btps. no tripping at gazipur |
| 32 | 27.03.10 | 09.00 | 220kv panipat – narela ckt.-iii | 27.03.10 | 09.04 | ckt. tripped on 30c, e/f `b’ phase at narela. |
| 33 | 27.03.10 | 14.01 | 220kv mandola – wazirabad ckt-iv | 27.03.10 | 18.53 | ckt. tripped on generatl trip, dist prot `ryb’ phase fault loop l1-l2 at wazirabad. |
| 34 | 27.03.10 | 14.30 | 220kv wazirabad – kashmiri gate ckt-ii | 27.03.10 | 17.19 | ckt. tripped on gfc, stf wl1, wl2 at wazirabad. no tripping at kashmiri gate. |
| 35 | 27.03.10 | 15.27 | 220kv maharani bagh – sarita vihar ckt. | 27.03.10 | 15.47 | ckt. tripped on dist prot `r&b’ phase zone-i at maharani bagh and on dist prot `abc’ phase zone-i at sarita vihar. |
| 36 | 28.03.10 | 09.20 | 66/11kv 20mva pr. tr.-iii at najafgarh | 28.03.10 | 09.35 | tr. tripped on winding temp alarm 30b. |
| 37 | 29.03.10 | 02.59 | 220/66kv 160mva pr. tr. at gt | 29.03.10 | 13:15 | `y’ phase lead between 66kv cb and 160mva tr. flashed. |
| 38 | 29.03.10 | 23.45 | 66/11kv 20mva pr. tr.-iii at najafgarh | 29.03.10 | 23.58 | tr. tripped on winding temp alarm. |
| 39 | 30.03.10 | 00.33 | 66/11kv 20mva pr. tr.-iii at najafgarh | 29.03.10 | 07.53 | tr. tripped on winding temp alarm. |
| 40 | 30.03.10 | 10.20 | 66/11kv 20mva pr. tr.-iii at najafgarh | 29.03.10 | 11.10 | tr. tripped on 30b |

21	DETAILS OF UNDERFREQUENCY TRIPPINGS

| Sr. No | Date | Type of Relay | Time Out | Time IN | Name of the Grid S/Stn | Load in MW | Name of the Feeder |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 08.03.10 | FLAT MODE | 22:07 | 22:11 | OKHLA | 39 | OKHLA PH-II CKT. I & II, BALAJI CKT. I & II, NEHRU PLACE CKT.-IV |
| 2 | 13.03.10 | FLAT MODE | 10:14 | 10:55 | ROHTAK ROAD | 34 | VISHAL CKT, S.B.MILL CKT I & II, MADIPUR CKT, RAMA ROAD CKT. |
| 3 | 13.03.10 | FLAT MODE | 23:04 | 23:08 | NAJAFGARH | 27 | G-5 PAPANKALAN CKT. I &II, 20MVA PR. TR. –III |
| 4 | 16.03.10 | FLAT MODE | 5:20 | 5:25 | OKHLA | 15 | ALAKHNANDA CKT, TUGLAKABAD CKT. |
| 5 | 16.03.10 | FLAT MODE | 5:30 | 5:39 | OKHLA | 15 | ALAKHNANDA CKT., TUGLAKABAD CKT. |
| 6 | 16.03.10 | FLAT MODE | 5:20 | 5:39 | OKHLA | 15 | RAIL POLE BATRA CKT. |
| 7 | 16.03.10 | FLAT MODE | 5:18 | 5:43 | KASHMIRI GATE | 4 | JAMA MASJID CKT, TOWN HALL CKT. |
| 8 | 16.03.10 | FLAT MODE | 5:30 | 5:44 | SHALIMARBAGH | 18 | WAZIRPUR-I CKT, SMB KHOSLA CKT -II (O/H) |
| 9 | 17.03.10 | FLAT MODE | 20:48 | 20:57 | ROHINI | 24 | ROHINI -VI CKT. I & II |
| 10 | 17.03.10 | FLAT MODE | 23:04 | 23:50 | SUBZI MANDI | 10 | SHAHZADAWALA BAGH |
| 11 | 17.03.10 | FLAT MODE | 22:52 | 23:00 | KASHMIRI GATE | 11 | JAMA MASJID CKT, TOWN HALL CKT. |
| 13 | 18.03.10 | FLAT MODE | 0:01 | 0:30 | PUSA | 4 | PUSA |
| 14 | 18.03.10 | FLAT MODE | 0:01 | 0:30 | SUDARSHAN PARK | 6 | SUDARSHAN PARK |
| 15 | 18.03.10 | FLAT MODE | 0:01 | 0:30 | SARASWATI GARDEN | 8 | SARASWATI GARDEN |
| 16 | 18.03.10 | FLAT MODE | 10:15 | 11:15 | INDERPURI | 6 | INDERPURI |
| 17 | 18.03.10 | FLAT MODE | 11:48 | 12:05 | ROHTAK ROAD | 41 | VISHAL CKT-I, S.B.MILL CKT -II,, MADIPUR CKT, RAMA ROAD CKT. |
| 18 | 18.03.10 | FLAT MODE | 18:15 | 18:27 | SHALIMARBAGH | 24 | WAZIRPUR-II CKT. I &II |
| 19 | 18.03.10 | FLAT MODE | 20:21 | 20:54 | ROHINI | 75 | ROHINI SEC. 24 CKT. I & II |
| 20 | 18.03.10 | FLAT MODE | 21:04 | 21:55 | KASHMIRI GATE | 4 | 11KV LOAD AT KASHMIRI GATE |
| 21 | 18.03.10 | FLAT MODE | 21:08 | 21:55 | NARINA | 20 | REWARI LINE CKT, PAYAL CKT., 11KV LOAD AT NARAINA |
| 22 | 18.03.10 | FLAT MODE | 21:05 | 21:53 | ROHINI | 38 | ROHINI -VI CKT. I & II |
|  |  |  | 22:02 | 22:11 |  | 30 | ROHINI -VI CKT. I & II |
| 23 | 18.03.10 | FLAT MODE | 20:20 | 20:55 | VASANT KUNJ | 2 | 11KV LOAD AT VASANT KUNJ |

| Sr. No | Date | Type of Relay | Time Out | Time IN | Name of the Grid S/Stn | Load in MW | Name of the Feeder |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 24 | 18.03.10 | FLAT MODE | 21:05 | 21:53 | VASANT KUNJ | 1 | 11KV LOAD AT VASANT KUNJ |
| 25 | 18.03.10 | FLAT MODE | 21:20 | 20:20 | ROHTAK ROAD | 5 | ANAND PARVAT CKT, DMS CKT VISHAL CKT. -I |
| 26 | 18.03.10 | FLAT MODE | 20:22 | 20:55 | KASHMIRI GATE | 6 | FOUNTAIN CKT. -II |
| 27 | 19.03.10 | FLAT MODE | 5:18 | 6:15 | PITAMPURA-I | 2 | PITAMPURA-I |
| 28 | 19.03.10 | FLAT MODE | 5:19 | 6:16 | RANI BAGH | 7 | RANI BAGH |
| 29 | 19.03.10 | FLAT MODE | 5:20 | 6:17 | SANJAY GANDHI TR. NAGAR | 8 | SANJAY GANDHI TR. NAGAR |
| 30 | 19.03.10 | FLAT MODE | 5:21 | 6:18 | ROHINI -V | 5 | ROHINI –V |
| 31 | 19.03.10 | FLAT MODE | 11:45 | 12:10 | ROHTAK ROAD | 43 | RAMA ROAD CKT, VISHAL CKT, SHAHZADAWALA BAGH CKT, MADIPUR CKT, S.B.MILL CKT. |
| 32 | 19.03.10 | FLAT MODE | 4:40 | 4:58 | NAJAFGARH | 54 | BODELA -II CKT. I & II |
| 33 | 19.03.10 | FLAT MODE | 5:15 | 5:24 | NAJAFGARH | 6 | JAFFARPUR CKT. I & II |
| 34 | 19.03.10 | FLAT MODE | 5:31 | 5:58 | NAJAFGARH | 6 | JAFFARPUR CKT. I & II |
| 35 | 19.03.10 | FLAT MODE | 4:48 | 5:01 | GAZIPUR | 25 | KONDLI CKT. I & II, 11KV LOAD |
| 36 | 22.03.10 | FLAT MODE | 20:18 | 20:42 | OKHLA | 27 | OKHLA PH -I CKT. I & II, MASJID MOTH CKT. |
| 37 | 22.03.10 | FLAT MODE | 22:35 | 22:40 | OKHLA | 44 | MALVIYA NAGAR CKT. –III, ALAKH- NANDA CKT., TUGLAKABAD CKT. |
| 38 | 22.03.10 | FLAT MODE | 22:35 | 22:40 | KASHMIRI GATE | 7 | JAMA MASJID CKT, TOWN HALL CKT. |
| 39 | 22.03.10 | FLAT MODE | 22:35 | 22:40 | SHALIMARBAGH | 22 | WAZIRPUR-I CKT. 11KV LOAD AT SHALIMARBAGH |
| 40 | 23.03.10 | FLAT MODE | 23:48 | 23:55 | OKHLA | 44 | RAIL POLE BATRA CKT,, ALAKHNANDA CKT., TUGLAKABAD CKT. |
| 41 | 23.03.10 | FLAT MODE | 23:48 | 23:51 | KASHMIRI GATE | 8 | JAMA MASJID CKT, TOWN HALL CKT. |
| 42 | 23.03.10 | FLAT MODE | 23:47 | 23:51 | SHALIMARBAGH | 23 | WAZIRPUR-II CKT. –II SMB KHOSLA CKT. -II (O/H) |